## 协议说明
MODBUS协议说明
1 工作模式 | 1.1 格式
全部采用RTU方式,默认数据格式为1位开始位、8位数据位、无校验位、1位停止位。
1.2 通讯速率
默认为9600BPS，不可设
2.命令格式 | 2.1 功能码： 04
数据起始地址：40001－
数据长度：不大于125及最大寄存器数量
说明：读取模拟量。读取的是16位整数或者无符号整数
举例：
| MODBUS请求 | 十六进制 | MODBUS响应 | 十六进制
| 从机地址 | 01 | 从机地址 | 01
| 功能码 | 04 | 功能码 | 03
| 开始地址高字节 | 00 | 字节数 | 84
| 开始地址低字位 | 00 | 数据高字节（寄存器地址30001） | xx
| 寄存器数高字节 | 00 | 数据低字节（寄存器地址30001） | xx
| 寄存器数低字节 | 42 | 数据高字节（寄存器地址30002） | xx
| CRC低字节 | — | 数据低字节（寄存器地址30002） | xx
| CRC高字节 | — | 数据高字节（寄存器地址30003） | xx
|  |  | 数据低字节（寄存器地址30003） | xx
|  |  | ······· | ···
|  |  | 数据高字节（寄存器地址30066） | xx
|  |  | 数据低字节（寄存器地址30066） | xx
|  |  | CRC低字节 | —
|  |  | CRC高字节 | —
注意：MODBUS请求中寄存器地址需加1后等于MODBUS响应中的寄存器地址。
3 从机地址说明
地址为1-250个，可以任意设置；
在触摸屏上进行设置

## 中文版
功能码 | 寄存器地址（十进制） | Modscan32地址 | 单位 | 寄存器描述
4 | 0 | 30001 | 0.1Hz | 主电输入频率
4 | 1 | 30002 | 0.1V | 主电输入线电压Line1
4 | 2 | 30003 | 0.1V | 主电输入线电压Line2
4 | 3 | 30004 | 0.1V | 主电输入线电压Line3
4 | 4 | 30005 | 0.1V | 主电输入相电压Line1
4 | 5 | 30006 | 0.1V | 主电输入相电压Line2
4 | 6 | 30007 | 0.1V | 主电输入相电压Line3
4 | 7 | 30008 | 1A | 电池额定充电电流
4 | 8 | 30009 | 0.1KVA | 主电源输入容量
4 | 9 | 30010 | 0.1Hz | 输出频率
4 | 10 | 30011 | 0.1V | 输出线电压Line1
4 | 11 | 30012 | 0.1V | 输出线电压Line2
4 | 12 | 30013 | 0.1V | 输出线电压Line3
4 | 13 | 30014 | 0.1V | 输出相电压Line1
4 | 14 | 30015 | 0.1V | 输出相电压Line2
4 | 15 | 30016 | 0.1V | 输出相电压Line3
4 | 16 | 30017 | 0.1A | 输出相电流Line1
4 | 17 | 30018 | 0.1A | 输出相电流Line2
4 | 18 | 30019 | 0.1A | 输出相电流Line3
4 | 19 | 30020 | 0.1KVA | 输出相容量Line1
4 | 20 | 30021 | 0.1KVA | 输出相容量Line2
4 | 21 | 30022 | 0.1KVA | 输出相容量Line3
4 | 22 | 30023 | 0.1KVA | 输出相总容量
4 | 23 | 30024 | 0.1% | 输出相容量百分比Line1
4 | 24 | 30025 | 0.1% | 输出相容量百分比Line2
4 | 25 | 30026 | 0.1% | 输出相容量百分比Line3
4 | 26 | 30027 | 0.1Hz | 旁路频率
4 | 27 | 30028 | 0.1V | 旁路输入线电压Line1
4 | 28 | 30029 | 0.1V | 旁路输入线电压Line2
4 | 29 | 30030 | 0.1V | 旁路输入线电压Line3
4 | 30 | 30031 | 0.1V | 旁路输入相电压Line1
4 | 31 | 30032 | 0.1V | 旁路输入相电压Line2
4 | 32 | 30033 | 0.1V | 旁路输入相电压Line3
4 | 33 | 30034 | 0.1V | 直流电压
4 | 34 | 30035 | 0.1V | 电池电压
4 | 35 | 30036 | 0.1% | 电池容量百分比
4 | 36 | 30037 | 0.1A | 电池电流 | 电池放电电流
4 | 37 | 30038 | - | 空
4 | 38 | 30039 | 0.1℃ | 整流器温度
4 | 39 | 30040 | 0.1℃ | 系统温度
4 | 40 | 30041 | - | 空
4 | 41 | 30042 | 0.1℃ | 逆变器温度
4 | 42 | 30043 | 0.1% | 输入相电压百分比Line1
4 | 43 | 30044 | 0.1% | 输入相电压百分比Line2
4 | 44 | 30045 | 0.1% | 输入相电压百分比Line3
4 | 45 | 30046 | 0.1% | 输入相电流百分比Line1
4 | 46 | 30047 | 0.1% | 输入相电流百分比Line2
4 | 47 | 30048 | 0.1% | 输入相电流百分比Line3
4 | 48 | 30049 | 0.1A | 输入相电流Line1
4 | 49 | 30050 | 0.1A | 输入相电流Line2
4 | 50 | 30051 | 0.1A | 输入相电流Line3
4 | 51 | 30052 | 0.1V | 逆变输出电压
4 | 52 | 30053 | Min | 电池放电剩余时间
…… | …… |  | …… | ……
功能码 | 寄存器地址 | Modscan32地址 | 单位 | 寄存器描述 | 寄存器位 | 寄存器位描述
4 | 57 |  | - | 系统状态代码 | 0 | 电源卡错误
[5 empty] | 1 | RS232之DSR_ON讯号存在
[5 empty] | 2 | Configuration circuit not present
[5 empty] | 3 | 跳线（Jumper）CONFG2不存在
[5 empty] | 4 | 电池电压或整流器低电压
[5 empty] | 5 | 电池或者整流器低电压预警
[5 empty] | 6 | 电池接点开路
[5 empty] | 7 | 电池接点永久异常
[5 empty] | 8 | 系统卡电源错误
[5 empty] | 9 | 电源卡暂时错误
[5 empty] | 10 | 系统卡同步错误
[5 empty] | 11 | 系统卡侦测输出频率错误
[5 empty] | 12 | 系统温度过高
[5 empty] | 13 | 初始化错误
[5 empty] | 14 | 系统关机指令动作
[5 empty] | 15 | 系统卡辅助输入
4 | 58 |  | - | 负载状态 | 0 | -
[5 empty] | 1 | SWOUT 输出开关开启
[5 empty] | 2 | Line3 平均输出电压错误
[5 empty] | 3 | Line1 瞬间输出电压错误
[5 empty] | 4 | Line2 瞬间输出电压错误
[5 empty] | 5 | Line3 瞬间输出电压错误
[5 empty] | 6 | Line1 平均输出电压错误
[5 empty] | 7 | Line2 平均输出电压错误
[5 empty] | 8 | Line1 输出漏电流过高
[5 empty] | 9 | Line2 输出漏电流过高
[5 empty] | 10 | Line3 输出漏电流过高
[5 empty] | 11 | Line1 输出过载
[5 empty] | 12 | Line2 输出过载
[5 empty] | 13 | Line3 输出过载
[5 empty] | 14 | 永久过载
[5 empty] | 15 | TA DIFF，讯号存在
4 | 59 |  | - | 旁路状态 | 0 | 逆变器输出接点异常
[5 empty] | 1 | 逆变器输出接点开启
[5 empty] | 2 | 旁路接点闭锁 | 旁路开关状态
[5 empty] | 3 | 旁路接点异常
[5 empty] | 4 | 旁路SCR开关永久闭锁
[5 empty] | 5 | 旁路无效
[5 empty] | 6 | 逆变器输出接点异常永久关闭
[5 empty] | 7 | 切换至旁路命令动作
[5 empty] | 8 | 远程命令动作：切换至旁路（逆变器关闭）
[5 empty] | 9 | 旁路静态开关（SCR）异常
[5 empty] | 10 | 旁路输入电压Line No.1错误
[5 empty] | 11 | 旁路输入电压Line No.2错误
[5 empty] | 12 | 旁路输入电压Line No.3错误
[5 empty] | 13 | 旁路输入频率错误
[5 empty] | 14 | Sequence error in phase 1 and 2 at bypass Line input
[5 empty] | 15 | 手动开关SWB闭锁
4 | 60 |  | - | 整流器和电池状态 | 0 | Line3 无输入电流
[5 empty] | 1 | 整流器限功率动作
[5 empty] | 2 | 整流器调整错误
[5 empty] | 3 | 整流器输入频率错误
[5 empty] | 4 | 整流器过温
[5 empty] | 5 | 整流器输出电压过高
[5 empty] | 6 | 整流器输出电源错误
[5 empty] | 7 | 整流器停止工作
[5 empty] | 8 | Line1 输入电压过高
[5 empty] | 9 | Line2 输入电压过高
[5 empty] | 10 | Line3 输入电压过高
[5 empty] | 11 | Line1 输入电压过低 | 低输入电压
[5 empty] | 12 | Line2 输入电压过低
[5 empty] | 13 | Line3 输入电压过低
[5 empty] | 14 | Line1 无输入电流
[5 empty] | 15 | Line2 无输入电流
4 | 61 |  | - | 整流器和电池状态 | 0 | 整流器其中一回路（软件版本<152）
[5 empty] | 1 | SGP电源异常
[5 empty] | 2 | 手动旁路开关闭锁或者并联电缆错误
[5 empty] | 3 | -
[5 empty] | 4 | 整流器永久异常
[5 empty] | 5 | 整流器DRV1电压异常
[5 empty] | 6 | 整流器DRV2电压异常
[5 empty] | 7 | 整流器DRV3电压异常
[5 empty] | 8 | -
[5 empty] | 9 | -
[5 empty] | 10 | -
[5 empty] | 11 | -
[5 empty] | 12 | -
[5 empty] | 13 | -
[5 empty] | 14 | -
[5 empty] | 15 | -
4 | 62 |  | - | 逆变器状态 | 0 | 逆变器异常
[5 empty] | 1 | 旁路与逆变器不同步
[5 empty] | 2 | 逆变器自动复归（Auto Reset）
[5 empty] | 3 | Auxiliary feeder error for IGBT modules
[5 empty] | 4 | 逆变器输出电压过高
[5 empty] | 5 | 逆变器输入电压持续过高
[5 empty] | 6 | 逆变器sensor1 侦测到温度过高
[5 empty] | 7 | 逆变器sensor2 侦测到温度过高
[5 empty] | 8 | 指示灯的电线反向
[5 empty] | 9 | Lookup by card or module 3 in inverter
[5 empty] | 10 | Lookup by card or module 2 in inverter
[5 empty] | 11 | 瞬间过流
[5 empty] | 12 | 逆变器配接错误
[5 empty] | 13 | 逆变器电源错误
[5 empty] | 14 | parallel syncro fail* 并机异常
[5 empty] | 15 | 并联机中的主机
4 | 63 |  | - | 逆变器状态 | 0 | 逆变器sensor3 侦测到温度过高
[5 empty] | 1 | 锁机 （by card 或逆变器的木块1）
[5 empty] | 2 | parallel serial data fail
[5 empty] | 3 | 逆变器停止运作
[5 empty] | 4 | 逆变器输出交流电压过低
[5 empty] | 5 | 逆变器输出直流电压过低
[5 empty] | 6 | 逆变器手动复位
[5 empty] | 7 | 逆变器永久异常，指示灯电线反向
[5 empty] | 8 | -
[5 empty] | 9 | -
[5 empty] | 10 | -
[5 empty] | 11 | -
[5 empty] | 12 | -
[5 empty] | 13 | -
[5 empty] | 14 | -
[5 empty] | 15 | -
4 | 64 |  | - | 告警状态1 | 0 | 暂时或永久切换至旁路 | 旁路模式
[5 empty] | 1 | 旁路输出（VA）小于自动关机设定值
[5 empty] | 2 | 内部异常1：no circ configuration
[5 empty] | 3 | 内部异常2：逆变器锁住
[5 empty] | 4 | 内部异常3：输出接点
[5 empty] | 5 | 内部异常4：整流器锁住
[5 empty] | 6 | 内部异常5：旁路SCR
[5 empty] | 7 | 内部异常6：电源
[5 empty] | 8 | 旁路干扰
[5 empty] | 9 | 手动旁路开关SWMB动作
[5 empty] | 10 | 旁路电压异常或开关SWMB，FSCR开启
[5 empty] | 11 | 输入电压异常或开关SWIN开启
[5 empty] | 12 | 电池电压过低
[5 empty] | 13 | 输入电压过低或过载（功率）
[5 empty] | 14 | 电池放电或开关SWB开启
[5 empty] | 15 | 输出过载
4 | 65 |  | - | 告警状态2 | 0 | 温度过高或风扇异常 | 温度过高
[5 empty] | 1 | 输入相位错误
[5 empty] | 2 | SWOUT或SWMB闭锁但无输出
[5 empty] | 3 | 系统关机动作
[5 empty] | 4 | 远程关机指令动作
[5 empty] | 5 | memory changed：CODE=。。。。。。
[5 empty] | 6 | 内部错误11：逆变器或旁路输出连接
[5 empty] | 7 | 内部定时器停止
[5 empty] | 8 | 内部错误7：系统卡电源
[5 empty] | 9 | 内部错误8：整流器某一组线路
[5 empty] | 10 | 内部错误9：电池接点
[5 empty] | 11 | 内部错误10：逆变器-整流器间的讯号
[5 empty] | 12 | 旁路输出过载
[5 empty] | 13 | 旁路输出指令动作；
[5 empty] | 14 | 远程旁路指令动作
[5 empty] | 15 | -

## English
Function Code | Register Address | Unit | Register Description
4 | 0001H | 0.1Hz | Main input frequency
4 | 0002H | 0.1V | Main Input Line Voltage Line1
4 | 0003H | 0.1V | Main Input Line Voltage Line2
4 | 0004H | 0.1V | Main Input Line Voltage Line3
4 | 0005H | 0.1V | Main Input Phase Voltage Line1
4 | 0006H | 0.1V | Main Input Phase Voltage Line2
4 | 0007H | 0.1V | Main Input Phase Voltage Line3
4 | 0008H | 1A | Rated Charging Current of Batteries
4 | 0009H | 0.1KVA | Input capacity of main power supply
4 | 0010H | 0.1Hz | Output frequency
4 | 0011H | 0.1V | Output line voltage Line1
4 | 0012H | 0.1V | Output line voltage Line2
4 | 0013H | 0.1V | Output line voltage Line3
4 | 0014H | 0.1V | Output phase voltage Line1
4 | 0015H | 0.1V | Output phase voltage Line2
4 | 0016H | 0.1V | Output phase voltage Line3
4 | 0017H | 0.1A | Output phase current Line1
4 | 0018H | 0.1A | Output phase current Line2
4 | 0019H | 0.1A | Output phase current Line3
4 | 0020H | 0.1KVA | Output phase capacity Line1
4 | 0021H | 0.1KVA | Output phase capacity Line2
4 | 0022H | 0.1KVA | Output phase capacity Line3
4 | 0023H | 0.1KVA | Total output phase capacity
4 | 0024H | 0.1% | Output Phase Capacity Percentage Line1
4 | 0025H | 0.1% | Output Phase Capacity Percentage Line2
4 | 0026H | 0.1% | Output Phase Capacity Percentage Line3
4 | 0027H | 0.1Hz | Bypass frequency
4 | 0028H | 0.1V | Bypass Input Line 1
4 | 0029H | 0.1V | Bypass Input Line 2
4 | 0030H | 0.1V | Bypass Input Line 3
4 | 0031H | 0.1V | Bypass Input Phase Voltage Line1
4 | 0032H | 0.1V | Bypass Input Phase Voltage Line2
4 | 0033H | 0.1V | Bypass Input Phase Voltage Line3
4 | 0034H | 0.1V | DC voltage
4 | 0035H | 0.1V | Battery voltage
4 | 0036H | 0.1% | Percentage of battery capacity
4 | 0037H | 0.1A | Battery discharge current
4 | 0038H | - | empty
4 | 0039H | 0.1℃ | Rectifier temperature
4 | 0040H | 0.1℃ | System temperature
4 | 0041H | - | empty
4 | 0042H | 0.1℃ | Inverter temperature
4 | 0043H | 0.1% | Input Phase Voltage Percentage Line1
4 | 0044H | 0.1% | Input Phase Voltage Percentage Line2
4 | 0045H | 0.1% | Input Phase Voltage Percentage Line3
4 | 0046H | 0.1% | Input Phase Current Percentage Line1
4 | 0047H | 0.1% | Input Phase Current Percentage Line2
4 | 0048H | 0.1% | Input Phase Current Percentage Line3
4 | 0049H | 0.1A | Input phase current Line1
4 | 0050H | 0.1A | Input phase current Line2
4 | 0051H | 0.1A | Input phase current Line3
4 | 0052H | 0.1V | Inverter output voltage
4 | 0053H | Min | Remaining time of battery discharge
…… | …… | …… | ……
Function Code | Register Address | Unit | Register Description | BIT | Bit description
4 | 0058H | - | System status code | 0 | Power card error
|  |  |  | 1 | DSR_ON Signal Existence of RS232
|  |  |  | 2 | Configuration circuit not present
|  |  |  | 3 | Jumper CONFG2 does not exist
|  |  |  | 4 | Battery Voltage or Rectifier Low Voltage
|  |  |  | 5 | Low Voltage Early Warning for Batteries or Rectifiers
|  |  |  | 6 | Battery contacts open
|  |  |  | 7 | Permanent abnormality of battery contacts
|  |  |  | 8 | System Card Power Error
|  |  |  | 9 | Power card temporary error
|  |  |  | 10 | System Card Synchronization Error
|  |  |  | 11 | System Card Detecting Output Frequency Error
|  |  |  | 12 | System temperature is too high.
|  |  |  | 13 | Initialization error
|  |  |  | 14 | System shutdown command action
|  |  |  | 15 | System Card Auxiliary Input
4 | 0059H | - | Load state | 0 | empty
|  |  |  | 1 | SWOUT Output Switch on
|  |  |  | 2 | Line3 Average Output Voltage Error
|  |  |  | 3 | Line1 Instantaneous Output Voltage Error
|  |  |  | 4 | Line2 Instantaneous Output Voltage Error
|  |  |  | 5 | Line3 Instantaneous Output Voltage Error
|  |  |  | 6 | Line1 Average Output Voltage Error
|  |  |  | 7 | Line2 Average Output Voltage Error
|  |  |  | 8 | Line1 Output Leakage Current Excessive
|  |  |  | 9 | Line2 Output Leakage Current Excessive
|  |  |  | 10 | Line3 Output Leakage Current Excessive
|  |  |  | 11 | Line1 output overload
|  |  |  | 12 | Line2 output overload
|  |  |  | 13 | Line3 output overload
|  |  |  | 14 | Permanent overload
|  |  |  | 15 | TA DIFF, Signal Existence
4 | 0060H | - | Bypass state | 0 | Abnormal output contacts of inverters
|  |  |  | 1 | Inverter Output Contact Opening
|  |  |  | 2 | Bypass contact latch up
|  |  |  | 3 | Bypass contact exception
|  |  |  | 4 | Permanent Block of Bypass SCR Switch
|  |  |  | 5 | Bypass failure
|  |  |  | 6 | Abnormal permanent closure of output contacts of inverters
|  |  |  | 7 | Switch to bypass command action
|  |  |  | 8 | Remote Command Action: Switch to Bypass (Inverter Closed)
|  |  |  | 9 | Bypass Static Switch (SCR) Abnormality
|  |  |  | 10 | Bypass Input Voltage Line No.1 Error
|  |  |  | 11 | Bypass Input Voltage Line No.2 Error
|  |  |  | 12 | Bypass Input Voltage Line No.3 Error
|  |  |  | 13 | Bypass input frequency error
|  |  |  | 14 | Sequence error in phase 1 and 2 at bypass Line input
|  |  |  | 15 | SWB lock of manual switch
4 | 0061H | - | Rectifier and battery status | 0 | Line3 No Input Current
|  |  |  | 1 | Power Limiting Action of Rectifier
|  |  |  | 2 | Rectifier adjustment error
|  |  |  | 3 | Input frequency error of rectifier
|  |  |  | 4 | Over temperature rectifier
|  |  |  | 5 | Overvoltage of rectifier output
|  |  |  | 6 | Rectifier Output Power Source Error
|  |  |  | 7 | Rectifier stops working
|  |  |  | 8 | Line1 input voltage is too high
|  |  |  | 9 | Line2 input voltage is too high
|  |  |  | 10 | Line3 input voltage is too high
|  |  |  | 11 | Line1 Input Voltage Too Low
|  |  |  | 12 | Line2 Input Voltage Too Low
|  |  |  | 13 | Line3 Input Voltage Too Low
|  |  |  | 14 | Line1 No Input Current
|  |  |  | 15 | Line2 No Input Current
4 | 0062H | - | Rectifier and battery status | 0 | One of the primary circuits of the rectifier (software version < 152)
|  |  |  | 1 | SGP power abnormal
|  |  |  | 2 | Manual Bypass Switch Blocking or Parallel Cable Error
|  |  |  | 3 | empty
|  |  |  | 4 | Permanent anomaly of rectifier
|  |  |  | 5 | Rectifier DRV1 Voltage Abnormality
|  |  |  | 6 | Rectifier DRV2 Voltage Abnormality
|  |  |  | 7 | Rectifier DRV3 Voltage Abnormality
|  |  |  | 8 | empty
|  |  |  | 9 | empty
|  |  |  | 10 | empty
|  |  |  | 11 | empty
|  |  |  | 12 | empty
|  |  |  | 13 | empty
|  |  |  | 14 | empty
|  |  |  | 15 | empty
4 | 0063H | - | Inverter state | 0 | Inverter abnormal
|  |  |  | 1 | Bypass and Inverter Asynchronization
|  |  |  | 2 | Inverter Auto Reset
|  |  |  | 3 | Auxiliary feeder error for IGBT modules
|  |  |  | 4 | Inverter output voltage is too high
|  |  |  | 5 | Inverter Input Voltage Continuously Excessively High
|  |  |  | 6 | Inverter Sensor 1 detects excessive temperature
|  |  |  | 7 | Inverter Sensor 2 detects excessive temperature
|  |  |  | 8 | Reverse Wire of Indicator Lamp
|  |  |  | 9 | Lookup by card or module 3 in inverter
|  |  |  | 10 | Lookup by card or module 2 in inverter
|  |  |  | 11 | Transient overcurrent
|  |  |  | 12 | Inverter mismatch
|  |  |  | 13 | Inverter Power Error
|  |  |  | 14 | parallel syncro fail* 并机异常
|  |  |  | 15 | Host in Parallel Connection
4 | 0064H | - | Inverter state | 0 | Inverter Sensor 3 detects excessive temperature
|  |  |  | 1 | Locking machine (block 1 by card or inverter)
|  |  |  | 2 | parallel serial data fail
|  |  |  | 3 | The Inverter Stops Operating
|  |  |  | 4 | Inverter output AC voltage is too low
|  |  |  | 5 | Inverter output DC voltage is too low
|  |  |  | 6 | Manual Reset of Inverter
|  |  |  | 7 | Inverter permanent abnormality, indicator wire reverse
|  |  |  | 8 | empty
|  |  |  | 9 | empty
|  |  |  | 10 | empty
|  |  |  | 11 | empty
|  |  |  | 12 | empty
|  |  |  | 13 | empty
|  |  |  | 14 | empty
|  |  |  | 15 | empty
4 | 0065H | - | Alarm status 1 | 0 | Transient or permanent switch to bypass
|  |  |  | 1 | Bypass Output (VA) is less than the set value of automatic shutdown
|  |  |  | 2 | Internal anomaly 1 ：no circ configuration
|  |  |  | 3 | Internal Abnormality 2: Inverter Locking
|  |  |  | 4 | Internal Abnormality 3: Output contacts
|  |  |  | 5 | Internal Abnormality 4: rectifier lock
|  |  |  | 6 | Internal Abnormality 5: bypass SCR
|  |  |  | 7 | Internal Abnormality 6: power supply
|  |  |  | 8 | Bypass interference
|  |  |  | 9 | Manual bypass switch SWMB action
|  |  |  | 10 | Bypass Voltage Abnormal or Switch SWMB, FSCR Open
|  |  |  | 11 | Abnormal input voltage or switching SWIN on
|  |  |  | 12 | Low battery voltage
|  |  |  | 13 | Input voltage too low or overload (power)
|  |  |  | 14 | Battery discharge or switch SWB on
|  |  |  | 15 | over load
4 | 0066H | - | Alarm status 2 | 0 | Excessive temperature or fan abnormality
|  |  |  | 1 | Input phase error
|  |  |  | 2 | SWOUT or SWMB latch-up but no output
|  |  |  | 3 | System shutdown action
|  |  |  | 4 | Remote shutdown command action
|  |  |  | 5 | memory changed：CODE=。。。。。。
|  |  |  | 6 | Internal Abnormality 11: Inverter or Bypass Output Connection
|  |  |  | 7 | Internal timer stop
|  |  |  | 8 | Internal Error 7: System Card Power Supply
|  |  |  | 9 | Internal error 8: A group of rectifiers
|  |  |  | 10 | Internal error 9: Battery contacts
|  |  |  | 11 | Internal Error 10: Signal between Inverter and Rectifier
|  |  |  | 12 | Bypass output overload
|  |  |  | 13 | Bypass output command action;
|  |  |  | 14 | Remote bypass command action
|  |  |  | 15 | empty