## cover
GmbH Klimatechnik
Monitoring Dataprotocoll
Release V1.1
January 15 2001

## 1 long status
Long Status Request 1
Long Status Request (PC -> MC)
Byte # | Description | Range | Value | C1001/2 | C4000 | C5000
0 | controller id | 1..255 |  | x | x | x
1 | command id |  | 1 | x | x | x
2 | number of following bytes |  | 2 | x | x | x
3 | LB checksum | 0..255 |  | x | x | x
4 | HB checksum | 0..255 |  | x | x | x
The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2.
Long Status Request (MC -> PC)
Byte # | Description | Range | Value | C1001/2 | C4000 | C5000
0 | controller id | 1..255 |  | x | x | x
1 | command id |  | 1 | x | x | x
2 | number of following bytes |  | 137 | x | x | x
3 | LB watertemperature -input- | -50.0..+50.0 °C | -500..+500 |  | x | x
4 | HB %
5 | LB return air temperature -input- | 0.0..100.0°C | 0..1000 | x | x | x
6 | HB %
7 | LB supply air temperature -input- | 0.0..100.0°C | 0..1000 |  | x | x
8 | HB %
9 | LB return air humidity -input- | 0.0..100.0% | 0..1000 | x | x | x
10 | HB %
11 | LB supply air humidity -input- | 0.0..100.0% | 0..1000 |  | x | x
12 | HB %
13 | LB outside air temperature -input- | -50.0..+50.0 °C | -500..+500 |  | x | x
14 | HB %
15 | LB outside air humidity -input- | 0.0..100.0% | 0..1000 |  | x | x
16 | HB %
17 | temperature setpoint shift (±12.7°C) | ±127 | -127..+127 |  | x | x
18 | humidity setpoint shift (±12.7%) | ±127 | -127..+127 |  | x | x
19 | - reserved -
20 | - reserved -
21 | - reserved -
22 | modul 1 - 4 digital out compressor 2 | bit-coded | see table |  |  | x
23 | modul 1 - 4 digital in compressor 2 | bit-coded | see table |  |  | x
24 | SW-Version |  |  |  | x | x
25 | module 1 digital out status byte 1 | bit-coded | see table | x | x | x
26 | module 1 digital out status byte 2 | bit-coded | see table | x | x | x
27 | module 2 digital out status byte 1 | bit-coded | see table | x | x | x
28 | module 2 digital out status byte 2 | bit-coded | see table | x | x | x
29 | module 3 digital out status byte 1 | bit-coded | see table |  | x | x
30 | module 3 digital out status byte 2 | bit-coded | see table |  | x | x
31 | module 4 digital out status byte 1 | bit-coded | see table |  | x | x
32 | module 4 digital out status byte 2 | bit-coded | see table |  | x | x
33 | module 1 digital in status byte 1 | bit-coded | see table | x | x | x
34 | module 1 digital in status byte 2 | bit-coded | see table | x | x | x
35 | module 2 digital in status byte 1 | bit-coded | see table | x | x | x
36 | module 2 digital in status byte 2 | bit-coded | see table |  | x | x
37 | module 3 digital in status byte 1 | bit-coded | see table |  | x | x
38 | module 3 digital in status byte 2 | bit-coded | see table |  | x | x
39 | module 4 digital in status byte 1 | bit-coded | see table |  | x | x
40 | module 4 digital in status byte 2 | bit-coded | see table |  | x | x
41 | analogue out GE/CW valve (module 1) | 0-100% | 0..255 | x | x | x
42 | analogue out PWW heating (module 1) | 0-100% | 0..255 |  | x | x
43 | analogue out humidifier (module 1) | 0-100% | 0..255 |  | x | x
44 | analogue out suction valve module 1 | 0-100% | 0..255 |  | x | x
45 | analogue out suction valve module 2 | 0-100% | 0..255 |  | x | x
46 | analogue out suction valve module 3 | 0-100% | 0..255 |  | x | x
47 | analogue out suction valve module 4 | 0-100% | 0..255 |  | x | x
48 | setpoint temperature | 10.0-35.0°C | 0..250 | x | x | x
49 | setpoint humidity | 10-90% | 10..90 | x | x | x
50 | year | 0..99 | 0..99 |  | x | x
51 | month | 1..12 | 1..12 |  | x | x
52 | day | 1..31 | 1..31 |  | x | x
53 | hour | 0..23 | 0..23 |  | x | x
54 | minute | 0..59 | 0..59 |  | x | x
55 | return air temp. too high alarm | 0..30°C | 0..30 | x | x | x
56 | supply air temp. too high alarm | 0..30°C | 0..30 |  | x | x
57 | return air temp. too low alarm | 0..30°C | 0..30 | x | x | x
58 | supply air temp. too low alarm | 0..30°C | 0..30 |  | x | x
59 | water temp. too high alarm | 0..50°C | 0..50 |  | x | x
60 | water temp. too low alarm | -50..+30°C | 0..80 |  | x | x
61 | return air humid. too high alarm | 0..90% | 0..90 | x | x | x
62 | supply air humid. too high alarm | 0..90% | 0..90 |  | x | x
63 | return air humid. too low alarm | 0..90% | 0..90 | x | x | x
64 | supply air humid. too low alarm | 0..90% | 0..90 |  | x | x
------------------------------------- d a t a m o d u l e 1 -----------------------------------------
65 | compressor start (setpoint + val) | 0.0..10.0 K | 0..100 | x | x | x
66 | compressor hysteresis | 0.0..10.0 K | 0..100 | x | x | x
67 | suction valve start | 0.0..10.0 K | 0..100 |  | x | x
68 | suction valve proportional band | 0.0..10.0 K | 0..100 |  | x | x
69 | drycooler start temperature | 0..45°C | 0..45 |  | x | x
70 | drycooler enable temperature | 0..45°C | 0..45 |  | x
71 | glycol-pump start temperature | 0.0..10.0 K | 0..100 |  | x | x
72 | GE/CW valve off temperature | 0..35°C | 0..35 |  | x | x
73 | GE/CW valve start temperature | 0.0..10.0 K | 0..100 | x | x | x
74 | GE/CW valve proportional band | 0.0..10.0 K | 0..100 | x | x | x
75 | reheat 1 start temperature | 0.0..10.0 K | 0..100 | x | x | x
76 | reheat 1 hysteresis | 0.0..10.0 K | 0..100 | x | x | x
77 | reheat 2 start temperature | 0.0..10.0 K | 0..100 | x | x | x
78 | reheat 2 hysteresis | 0.0..10.0 K | 0..100 | x | x | x
79 | reheat 3 start temperature | 0.0..10.0 K | 0..100 |  | x | x
80 | reheat 3 hysteresis | 0.0..10.0 K | 0..100 |  | x | x
81 | PWW valve start temperature | 0.0..10.0 K | 0..100 |  | x | x
82 | PWW valve proportional band | 0.0..10.0 K | 0..100 |  | x | x
83 | dehumidification start | 0..90% | 0..90 | x | x | x
84 | dehumidification hysteresis | 0..90% | 0..90 | x | x | x
85 | humidification start | 0..90% | 0..90 | x | x | x
86 | humidification hysteresis | 0..90% | 0..90 | x | x | x
87 | humidification start (analogue) | 0..90% | 0..90 |  | x | x
88 | humidification proportional band (analogue) | 0..90% | 0..90 |  | x | x
------------------------------------- d a t a m o d u l e 2 -----------------------------------------
89 | compressor start (setpoint + val) | 0.0..10.0 K | 0..100 | x | x | x
90 | compressor hysteresis | 0.0..10.0 K | 0..100 | x | x | x
91 | suction valve start | 0.0..10.0 K | 0..100 |  | x | x
92 | suction valve proportional band | 0.0..10.0 K | 0..100 |  | x | x
93 | drycooler start temperature | 0..45°C | 0..45 |  | x | x
94 | reheat 1 start temperature | 0.0..10.0 K | 0..100 | x | x | x
95 | reheat 1 hysteresis | 0.0..10.0 K | 0..100 | x | x | x
96 | reheat 2 start temperature | 0.0..10.0 K | 0..100 | x | x | x
97 | reheat 2 hysteresis | 0.0..10.0 K | 0..100 | x | x | x
98 | reheat 3 start temperature | 0.0..10.0 K | 0..100 |  | x | x
99 | reheat 3 hysteresis | 0.0..10.0 K | 0..100 |  | x | x
100 | dehumidification start | 0..90% | 0..90 | x | x | x
101 | dehumidification hysteresis | 0..90% | 0..90 | x | x | x
102 | humidification start | 0..90% | 0..90 | x | x | x
103 | humidification hysteresis | 0..90% | 0..90 | x | x | x
------------------------------------- d a t a m o d u l e 3 -----------------------------------------
104 | compressor start (setpoint + val) | 0.0..10.0 K | 0..100 | x | x | x
105 | compressor hysteresis | 0.0..10.0 K | 0..100 | x | x | x
106 | suction valve start | 0.0..10.0 K | 0..100 |  | x | x
107 | suction valve proportional band | 0.0..10.0 K | 0..100 |  | x | x
108 | drycooler start temperature | 0..45°C | 0..45 |  | x | x
109 | reheat 1 start temperature | 0.0..10.0 K | 0..100 | x | x | x
110 | reheat 1 hysteresis | 0.0..10.0 K | 0..100 | x | x | x
111 | reheat 2 start temperature | 0.0..10.0 K | 0..100 | x | x | x
112 | reheat 2 hysteresis | 0.0..10.0 K | 0..100 | x | x | x
113 | reheat 3 start temperature | 0.0..10.0 K | 0..100 |  | x | x
114 | reheat 3 hysteresis | 0.0..10.0 K | 0..100 |  | x | x
115 | dehumidification start | 0..90% | 0..90 | x | x | x
116 | dehumidification hysteresis | 0..90% | 0..90 | x | x | x
117 | humidification start | 0..90% | 0..90 | x | x | x
118 | humidification hysteresis | 0..90% | 0..90 | x | x | x
------------------------------------- d a t a m o d u l e 4 -----------------------------------------
119 | compressor start (setpoint + val) | 0.0..10.0 K | 0..100 | x | x | x
120 | compressor hysteresis | 0.0..10.0 K | 0..100 | x | x | x
121 | suction valve start | 0.0..10.0 K | 0..100 |  | x | x
122 | suction valve proportional band | 0.0..10.0 K | 0..100 |  | x | x
123 | drycooler start temperature | 0..45°C | 0..45 |  | x | x
124 | reheat 1 start temperature | 0.0..10.0 K | 0..100 | x | x | x
125 | reheat 1 hysteresis | 0.0..10.0 K | 0..100 | x | x | x
126 | reheat 2 start temperature | 0.0..10.0 K | 0..100 | x | x | x
127 | reheat 2 hysteresis | 0.0..10.0 K | 0..100 | x | x | x
128 | reheat 3 start temperature | 0.0..10.0 K | 0..100 |  | x | x
129 | reheat 3 hysteresis | 0.0..10.0 K | 0..100 |  | x | x
130 | dehumidification start | 0..90% | 0..90 | x | x | x
131 | dehumidification hysteresis | 0..90% | 0..90 | x | x | x
132 | humidification start | 0..90% | 0..90 | x | x | x
133 | humidification hysteresis | 0..90% | 0..90 | x | x | x
------------------------------------- g e n e r a l d a t a -----------------------------------------
134 | general status byte 1 | bit-coded | see table | x | x | x
135 | general status byte 2 | bit-coded | see table | x | x | x
136 | error byte 1 | bit-coded | see table | x | x | x
137 | error byte 2 | bit-coded | see table | x | x | x
138 | LB checksum | 0..255 |  | x | x | x
139 | HB checksum | 0..255 |  | x | x | x
The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 137.
Bit # | General Status Byte 1 | POS | R / W | C1001/2 | C4000 | C5000
0 | 0 = PC-STOP (monitoring), 1 = on | 0x01 | R/W | x | x | x
1 | 0 = REMOTE STOP (contact), 1 = on | 0x02 | R | x | x | x
2 | 0 = LOCAL STOP (key), 1 = on | 0x04 | R | x | x | x
3 | 0 = TIMER-STOP (weekly oper.), 1 = on | 0x08 | R |  |  | x
4 | not used | 0x10 | R
5 | not used | 0x20 | R
6 | not used | 0x40 | R
7 | not used | 0x80 | R
NOTE: only if bits #0 to #3 are set to 1 the unit is in operation.
If one of the bits #0,#1,#2,#3 is set to 0 the unit is in STOP condition.
Bit # | General Status Byte 2 | POS | R / W | C1001/2 | C4000 | C5000
0 | not used | 0x01 | R
1 | not used | 0x02 | R
2 | not used | 0x04 | R
3 | not used | 0x08 | R
4 | not used | 0x10 | R
5 | not used | 0x20 | R
6 | not used | 0x40 | R
7 | not used | 0x80 | R
Bit # | module 1 - 4 digital OUT compressor 2 | POS | R / W | C1001/2 | C4000 | C5000
0 | modul 1 compressor 2 | 0x01 | R |  |  | x
1 | modul 2 compressor 2 | 0x02 | R |  |  | x
2 | modul 3 compressor 2 | 0x04 | R |  |  | x
3 | modul 4 compressor 2 | 0x08 | R |  |  | x
4 | not used | 0x10 | R |  |  | x
5 | not used | 0x20 | R |  |  | x
6 | not used | 0x40 | R |  |  | x
7 | not used | 0x80 | R |  |  | x
NOTE: if a bit is set to 1, than the corresponding component is in operation.
Bit # | module x digital OUT status byte 1 | POS | R / W | C1001/2 | C4000 | C5000
0 | reheat 1 | 0x01 | R | x | x | x
1 | compressor | 0x02 | R | x | x | x
2 | humidification | 0x04 | R | x | x | x
3 | dehumidification | 0x08 | R | x | x | x
4 | fan | 0x10 | R | x | x | x
5 | drycooler | 0x20 | R |  | x | x
6 | alarm relays #1 | 0x40 | R | x | x | x
7 | hot gas reheat / reheat 3 | 0x80 | R |  | x | x
NOTE: if a bit is set to 1, than the corresponding component is in operation.
Bit # | module x digital OUT status byte 2 | POS | R / W | C1001/2 | C4000 | C5000
0 | reheat 2 | 0x01 | R | x | x | x
1 | glycol pump | 0x02 | R |  | x | x
2 | louver (0=closed, 1=open) | 0x04 | R | x | x | x
3 | alarm relays #2 | 0x08 | R |  | x | x
4 | alarm relays #3 | 0x10 | R |  | x
5 | alarm relays #4 | 0x20 | R |  | x
6 | alarm relays #5 | 0x40 | R |  | x
7 | glycol pump 1 / 2 select | 0x80 | R |  | x | x
NOTE: if a bit is set to 1, than the corresponding component is in operation.
Bit # | module 1 - 4 digital IN compressor 2 | POS | R / W | C1001/2 | C4000 | C5000
0 | modul 1 compressor 2 low pressure | 0x01 | R |  |  | x
1 | modul 1 compressor 2 high pressure | 0x02 | R |  |  | x
2 | modul 2 compressor 2 low pressure | 0x04 | R |  |  | x
3 | modul 2 compressor 2 high pressure | 0x08 | R |  |  | x
4 | modul 3 compressor 2 low pressure | 0x10 | R |  |  | x
5 | modul 3 compressor 2 high pressure | 0x20 | R |  |  | x
6 | modul 4 compressor 2 low pressure | 0x40 | R |  |  | x
7 | modul 4 compressor 2 high pressure | 0x80 | R |  |  | x
NOTE: if a bit is set to 1, than the corresponding alarm is active.
Bit # | module x digital IN status byte 1 | POS | R / W | C1001/2 | C4000 | C5000
0 | compressor low pressure | 0x01 | R | x | x | x
1 | compressor high pressure | 0x02 | R | x | x | x
2 | reheat 1 failure | 0x04 | R | x | x | x
3 | humidification failure | 0x08 | R | x | x | x
4 | air flow failure | 0x10 | R | x | x | x
5 | filter clogged | 0x20 | R | x | x | x
6 | aux. alarm #1 | 0x40 | R | x | x | x
7 | reheat 2 failure | 0x80 | R | x | x | x
NOTE: if a bit is set to 1, than the corresponding alarm is active.
Bit # | module x digital IN status byte 2 | POS | R / W | C1001/2 | C4000 | C5000
0 | conductivity too high (< 5µS) | 0x01 | R |  | x | x
1 | ultrasonic failure | 0x02 | R |  | x | x
2 | glycol pump 1 failure | 0x04 | R |  | x | x
3 | glycol pump 2 failure | 0x08 | R |  | x | x
4 | drycooler failure | 0x10 | R |  | x | x
5 | water detector | 0x20 | R | x | x
6 | aux. alarm #2 | 0x40 | R |  | x | x
7 | aux. alarm #3 | 0x80 | R |  | x | x
NOTE: if a bit is set to 1, than the corresponding alarm is active.
Bit # | error byte 1 | POS | R / W | C1001/2 | C4000 | C5000
0 | return air temp. too high alarm | 0x01 | R | x | x | x
1 | return air humid. too high alarm | 0x02 | R | x | x | x
2 | supply air temp. too high alarm | 0x04 | R |  | x | x
3 | supply air humid. too high alarm | 0x08 | R |  | x | x
4 | water temp. too high alarm | 0x10 | R |  | x | x
5 | return air temp. too low alarm | 0x20 | R | x | x | x
6 | return air humid. too low alarm | 0x40 | R | x | x | x
7 | supply air temp. too low alarm | 0x80 | R |  | x | x
NOTE: if a bit is set to 1, than the corresponding alarm is active.
Bit # | error byte 2 | POS | R / W | C1001/2 | C4000 | C5000
0 | supply air humid. too low alarm | 0x01 | R |  | x | x
1 | water temp. too low alarm | 0x02 | R |  | x | x
2 | supervisor failure | 0x04 | R |  | x | x
3 | freeze alarm | 0x08 | R |  | x | x
4 | fire / smoke detector | 0x10 | R | x | x | x
5 | sensor failure | 0x20 | R | x | x | x
6 | controller failure | 0x40 | R | x | x | x
7 | IO-board transmission failure | 0x80 | R |  | x | x
NOTE: if a bit is set to 1, than the corresponding alarm is active.