## Worksheet
名称 | 编码 | 图标 | 设备可控 | 控制选项 | 属性 | 型号
温湿度传感器 | 1280 | icon-dial2 | 0 |  | {"as_time":"08:00~08:05","tn_field":"Tem","host_ip":"192.168.0.161","Tem":"℃","monitor":"istatus,温湿度状态,,;Tem,温度,0,℃;Hum,湿度,0,%","figure":",istatus,,;dial3,Tem,50,℃;dial3,Hum,100,%","exhibition":"istatus,温湿度状态,;Tem,温度,℃;Hum,湿度,%","briefing":"Tem,温度,℃;Hum,湿度,%","chart":"Tem,温度,℃;Hum,湿度,%","history":"Tem,温度,℃;Hum,湿度,%","statistics":"Tem","coefficient":"Tem,0.1;Hum,0.1"} | 1
定位漏水控制器 | 1536 | icon-water | 0 |  | {"monitor":"istatus,定位漏水状态,4,;LineRB,红黑线状态,4,;LineYG,黄绿线状态,4,;Lmd,灵敏度,,;Cable,线缆长度,0,米","figure":"11,istatus,,;,LineRB,,;,LineYG,,;,Lmd,,;,Cable,,米","exhibition":"istatus,定位漏水状态,","briefing":"istatus,定位漏水状态,","history":"istatus,定位漏水状态,","re_istatus":"0,正常;1,告警"} | 1
区域漏水控制器（485方式） | 1536 | icon-water | 0 |  | {"monitor":"istatus,漏水状态,,;Status,漏水状态,4,","figure":",istatus,,;27,Status,1,","exhibition":"istatus,漏水状态,","briefing":"istatus,漏水状态,","chart":"istatus,漏水状态,","re_Status":"0,正常;1,告警"} | 2
空调控制器（单机版） | 1792 | icon-kongtiao3 | 1 | state;开关机;onoff;0;0,1;null ext3;温度;processbar;26;18,30;℃;tem mode;模式;radiogroup;制冷;制冷,制热;null btn;操作;button | {"monitor":"istatus,空调控制器,,;Hfkwd,回风温度,0,℃;Sfkwd,送风温度,0,℃;Ht,上限温度,,;Lt,下限温度,,;Ct,设置温度,,;Dl,当前电流,,A;Hdl,电流上限,,A;Ldl,电流下限,,A;StatusV,当前状态,4,","figure":",istatus,,;05,Hfkwd,50,℃;06,Sfkwd,50,℃;,Ht,,;,Lt,,;,Ct,,;,Dl,,A;,Hdl,,A;,Ldl,,A;03,StatusV,,","exhibition":"istatus,空调控制器,;Hfkwd,回风温度,℃;Sfkwd,送风温度,℃","briefing":"Hfkwd,回风温度,℃;Sfkwd,送风温度,℃;StatusV,当前状态,","chart":"istatus,空调控制器,","coefficient":"Hfkwd,0.01;Sfkwd,0.01;Dl,0.01;Hdl,0.01;Ldl,0.01","re_StatusV":"0,关机;1,制冷;2,制热"} | 1
艾默生精密空调PEX系列 | 2049 | icon-kongtiao4 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,精密空调状态,,;tem,室内温度,0,℃;hum,室内湿度,0,%;va,A相电压,,V;vb,B相电压,,V;vc,C相电压,,V;c,加湿器电流,,A;pl,电源频率,,;hftemset,回风温度设定点,,℃;temset,送风温度设定点,,℃;temoff,温度偏差,,℃;humoff,湿度偏差,,;temdead,温度死区,,;humdead,湿度死区,,;htemw,高温告警值,,;ltemw,低温告警值,,;hhumw,高湿告警值,,;lhumw,低湿告警值,,;sftemw,送风高温告警值,,;sftemset,送风温度设定点,,;status,空调状态,,;warn,报警状态,,;stfansw,风机输出开关状态,,;sthumisw,加湿器输出开关状态,,;stcomp1sw,压缩机1输出开关状态,,;stcomp2sw,压缩机2输出开关状态,,;stheater1sw,加热1输出开关状态,,;stheater2sw,加热2输出开关状态,,;stalmswsw,公共报警输出开关状态,,;stwbybass1sw,液路旁通1输出开关状态,,;stwbybass2sw,液路旁通2输出开关状态,,;stwatersw,注水输出开关状态,,;stdehumisw,除湿输出开关状态,,;streservesw,备用输出开关状态,,;stcomp1ressw,压缩机1反相输出开关状态,,;stcomp2ressw,压缩机2反相输出开关状态,,;stcool,制冷状态,,;stheat,加热状态,,;stdehumi,除湿状态,,;sthumi,加湿状态,,","figure":",istatus,,;dial3,tem,,℃;dial3,hum,,%;,va,,V;,vb,,V;,vc,,V;,c,,A;,pl,,;,hftemset,,℃;,temset,,℃;,temoff,,℃;,humoff,,;,temdead,,;,humdead,,;,htemw,,;,ltemw,,;,hhumw,,;,lhumw,,;,sftemw,,;,sftemset,,;,status,,;,warn,,;,stfansw,,;,sthumisw,,;,stcomp1sw,,;,stcomp2sw,,;,stheater1sw,,;,stheater2sw,,;,stalmswsw,,;,stwbybass1sw,,;,stwbybass2sw,,;,stwatersw,,;,stdehumisw,,;,streservesw,,;,stcomp1ressw,,;,stcomp2ressw,,;,stcool,,;,stheat,,;,stdehumi,,;,sthumi,,","exhibition":"istatus,精密空调状态,;tem,室内温度,℃;hum,室内湿度,%"} | 0
机柜空调 | 2111 | icon-kongtiao3 | 0 |  | {"as_time":"08:00~08:05","tn_field":"tem"} | 0
声光报警器 | 2304 | icon-23 | 1 |  | {"iDo":"1"} | 0
DO1控制 | 2304 | icon-23 | 0 |  | {"as_time":"08:00~08:05"} | 1
DO2控制 | 2304 | icon-23 | 0 |  | {"host_ip":"192.168.0.161","as_time":"08:00~08:05"} | 2
三相电量仪 | 256 | icon-18 | 0 |  | {"monitor":"istatus,市电状态,,;Ygzdn,总电能,,KWH;Zyggl,总有功功率,,W;Zwggl,总无功功率,,Var;Zszgl,总视载功率,,VA;Zglys,总功率因素,,;Ady,A相电压,0,V;Bdy,B相电压,0,V;Cdy,C相电压,0,V;Adl,A相电流,0,A;Bdl,B相电流,0,A;Cdl,C相电流,0,A","figure":",istatus,,;,Ygzdn,,KWH;,Zyggl,,W;,Zwggl,,Var;,Zszgl,,VA;,Zglys,,;meter,Ady,300,V;meter,Bdy,300,V;meter,Cdy,300,V;meter,Adl,100,A;meter,Bdl,100,A;meter,Cdl,100,A","exhibition":"istatus,市电状态,;Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","briefing":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V;Adl,A相电流,A;Bdl,B相电流,A;Cdl,C相电流,A","history":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","coefficient":"Ygzdn,0.001;Zglys,0.001;Ady,0.1;Bdy,0.1;Cdy,0.1;Adl,0.01;Bdl,0.01;Cdl,0.01","re_istatus":"1,正常;0,告警"} | 0
单相电量仪 | 256 | icon-18 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,市电状态,,;Ygzdn,总电能,,KWH;Ayggl,有功功率,,W;Awggl,无功功率,,Var;Aszgl,视在功率,,VA;Aglys,功率因数,,;Ady,电压,0,V;Adl,电流,0,A","figure":",istatus,,;,Ygzdn,,KWH;,Ayggl,,W;,Awggl,,Var;,Aszgl,,VA;,Aglys,,;meter,Ady,300,V;meter,Adl,50,A","exhibition":"istatus,市电状态,;Ady,电压,V;Adl,电流,A","briefing":"Ady,电压,V;Adl,电流,A","statistics":"Ygzdn;Ady;Adl","coefficient":"Ygzdn,0.001;Ayggl,0.1;Awggl,0.1;Aszgl,0.1;Ady,0.1;Adl,0.1"} | 35
NVR | 3078 | icon-19 | 0 |  | {"as_time":"08:00~08:05"} | 0
门禁 | 3331 | icon-16 | 0 |  | {"as_time":"08:00~08:05","monitor":"Door,,,","figure":",istatus,,;,Rec,,;,Card,,;29,Door,,;,St,,;,LogDate,,","exhibition":"Door,,","chart":"Door,,","statistics":"Door","eq_log":"istatus,;Rec,;Card,;Door,;St,;LogDate,"} | 0
ping ip | 3335 | icon-host2 | 0 |  | {"monitor":"iPingState,IP状态,4,","figure":",istatus,,;,iPingState,,","exhibition":"iPingState,IP状态,","re_iPingState":"1,在线;0,离线"} | 0
红外探测器 | 3590 | icon-hongwai2 | 0 |  | {"monitor":"istatus,红外状态,4,","figure":"14,istatus,1,","exhibition":"istatus,红外状态,","briefing":"istatus,红外状态,"} | 0
烟雾探测器 | 3591 | icon-20 | 0 |  | {"1122":"111","as_time":"08:00~08:05","monitor":"istatus,烟感状态,4,","figure":"13,istatus,1,","exhibition":"istatus,烟感状态,","briefing":"istatus,烟感状态,","re_istatus":"0,正常;1,告警"} | 0
区域漏水控制器（开关量） | 3592 | icon-water | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,漏水监测,4,","figure":"12,istatus,1,","exhibition":"istatus,漏水监测,","briefing":"istatus,漏水监测,"} | 0
门磁开关 | 3593 | icon-15 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,门磁状态,4,","figure":",istatus,,","exhibition":"istatus,门磁状态,","chart":"istatus,门磁状态,","eq_log":"istatus,门磁状态"} | 0
防雷监测 | 3596 | icon-ec4 | 0 |  | {"as_time":"08:00~08:05"} | 0
蓄电池监测（管理模块） | 4609 | icon-ec2 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,蓄电池状态,,;V40004,蓄电池1#,0,V;V40005,蓄电池2#,0,V;V40006,蓄电池3#,0,V;V40307,蓄电池内阻1#,0,MΩ;V40308,蓄电池2#,0,MΩ;V40309,蓄电池3#,0,MΩ;V40910,蓄电池温度1#,0,℃;V40911,蓄电池温度2#,0,℃;V40912,蓄电池温度3#,0,℃;V41817,电池组电压,0,V;V41818,充放电电流,0,A;V41821,环境温度,0,℃;V41823,最高电压电池,,#;V41824,最低电压电池,,#;V41825,最高内阻电池,,#;V41826,电压均差值,,MV;V41827,电压均差值,,MV;V41833,整组状态,4,","figure":",istatus,,;,V40004,,V;,V40005,,V;,V40006,,V;,V40007,,V;,V40307,,MΩ;,V40308,,MΩ;,V40309,,MΩ;,V40310,,MΩ;,V40910,,℃;,V40911,,℃;,V40912,,℃;,V40913,,℃;meter,V41817,100,V;meter,V41818,50,A;,V41821,,℃;,V41823,,#;,V41824,,#;,V41825,,#;,V41826,,MV;,V41827,,MV;,V41833,,","exhibition":"istatus,蓄电池状态,;V41817,电池组电压,V;V41818,充放电电流,A","chart":"V40004,蓄电池1#,V;V40005,蓄电池2#,V;V40006,蓄电池3#,V;V40307,蓄电池内阻1#,MΩ;V40308,蓄电池2#,MΩ;V40309,蓄电池3#,MΩ;V40310,蓄电池4#,MΩ;V40910,蓄电池温度1#,℃;V40911,蓄电池温度2#,℃;V40912,蓄电池温度3#,℃","coefficient":"V40004,0.001;V40005,0.001;V40006,0.002;V40007,0.001;V40307,0.001;V40308,0.001;V40309,0.001;V40310,0.001;V40910,0.1;V40911,0.1;V40912,0.1;V40913,0.1;V41817,0.1;V41818,0.1","bar_0":"V400;电压;04;32;#e6e10e","bar_1":"V403;电阻;07;32;#34d417","bar_2":"V409;温度;10;32;#21d9f3","re_V41833":"0, 正常;1,告警"} | 0
配电空开监测仪 | 512 | icon-ec4 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,配电检测状态,,;sd1,空开1,4,;sd2,空开2,4,;sd3,空开3,4,;sd4,空开4,4,;sd5,空开5,4,;sd6,空开6,4,","figure":",istatus,,;01,sd1,0,;01,sd2,0,;01,sd3,0,;01,sd4,0,;01,sd5,0,;01,sd6,0,","exhibition":"istatus,配电检测状态,","briefing":"sd1,空开1,;sd2,空开2,;sd3,空开3,;sd4,空开4,;sd5,空开5,;sd6,空开6,","re_sd1":"0,闭合;1,断开","re_sd2":"0,闭合;1,断开","re_sd3":"0,闭合;1,断开","re_sd4":"0,闭合;1,断开","re_sd5":"0,闭合;1,断开","re_sd6":"0,闭合;1,断开"} | 0
山特3KVA UPS | 768 | icon-22 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,UPS状态,,;Vin1,输入电压,0,V;Fin,输入频率,,Hz;Vout,输出电压,0,V;Aout,输出负载,,%;Tem,环境温度,,℃;b7,蜂鸣器,,;b6,UPS状态,,;b5,UPS模式,,;b4,机型属性,,;b3,UPS故障,,;b2,旁路模式,,;b1,电池电压,,;b0,市电电压,,;Vbatt,电池电压,,V","figure":",istatus,,;meter,Vin1,300,V;,Fin,,Hz;meter,Vout,250,V;26,Aout,,%;,Tem,,℃;,b7,,;,b6,,;,b5,,;,b4,,;,b3,,;,b2,,;,b1,,;,b0,,;,Vbatt,,V","exhibition":"istatus,UPS状态,;Vin1,输入电压,V;Vout,输出电压,V","briefing":"Vin1,输入电压,V;Vout,输出电压,V;Aout,输出负载,%","coefficient":"Vin1,0.1;Fin,0.1;Vout,0.1;Aout,0.1;Tem,0.1;Vbatt,0.01","re_b7":"0,关闭;1,开启","re_b6":"0,关闭;1,开启","re_b5":"0,非测试;1,测试","re_b4":"0,在线式;1,后备式","re_b3":"0,否;1,是","re_b2":"0,否;1,是","re_b1":"0,正常;1,低电压","re_b0":"0,正常;1,异常"} | 0
微耕门禁 | 300000 | icon-16 | 0 |  | [] | 0
动环监控主机 | 0 | icon-17 | 0 |  | {"host_ip":"192.168.10.161","monitor":"cpu1,平均负载,,%;cpu5,近5分钟平均负载,,%;cpu15,近15分钟平均负载,,%;memtotal,总内存,,KB;memfree,剩余内存,,KB;membuf,缓冲内存,,KB;memcach,缓存内存,,KB","figure":",istatus,,;26,cpu1,100,%;26,cpu5,,%;26,cpu15,,%;,memtotal,512000,KB;,memfree,,KB;,membuf,,KB;,memcach,,KB","exhibition":"istatus,监控主机,","coefficient":"cpu1,0.1;cpu5,0.1;cpu15,0.1;memtotal,1;memfree,1;membuf,1;memcach,1"} | 0
海康视频 | 200000 | icon-19 | 0 |  | {"hk_ip":"182.0.0.","hk_port":"80","hk_username":"admin","hk_password":"admln12345","hk_channels":"1","hk_eqport":"8000"} | 0
萤石视频 | 100000 | icon-19 | 0 |  | {"hls":"1","deviceSerial":"1","channelNo":"1"} | 0
空调控制器 | 4944 | icon-kongtiao3 | 0 |  | {"monitor":"istatus,状态,,;V40001,当前湿度,0,%;V40002,当前温度,0,°C","figure":"03,istatus,,;28,V40001,,%;28,V40002,,°C","exhibition":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,°C","briefing":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,°C","history":"V40001,当前湿度,%;V40002,当前温度,°C","coefficient":"V40001,0.1;V40002,0.1"} | 1
网络监测 | 400000 | icon-17 | 0 |  | {"ping_ip":"192.168.0.161"} | 0
蓄电池监测（1180） | 1044 | icon-ec2 | 0 |  | {"monitor":"istatus,状态,,;Vol,电压,,V;Reg,内阻,,mΩ;Tem,温度,, ℃","figure":",istatus,,;,Vol0,,V;,Reg0,,mΩ;,Tem0,,℃;meter,Vol,,V;meter,Reg,,mΩ;,Tem,, ℃","coefficient":"Vol0,0.001;Reg0,0.0001;Tem0,0.01;Vol,0.001;Reg,0.0001;Tem,0.1","exhibition":"istatus,状态,","chart":"istatus,状态,","history":"istatus,状态,"} | 0
蓄电池监测 | 1029 | icon-ec2 | 0 |  | {"monitor":"istatus,电池电压,,V;Volt,电池电压t,,V;Vol1,电池电压1,,V;Vol22,电池电压22,,V;Vol2,电池电压2,,V;Vol3,电池电压3,,V","figure":",istatus,,V;,Volt,,V;,Vol1,,V;,Vol22,,V;,Vol2,,V;,Vol3,,V","coefficient":"istatus,0.1;Volt,0.1;Vol1,0.1;Vol22,0.1;Vol2,0.1;Vol3,0.1","bar_0":"Vol;电压;1;1;#e6e10e","bar_1":"Reg;内阻;1;1;#34d417","bar_2":"Tem;w温度;1;1;#21d9f3"} | 0
精密空调-艾默生 | 2056 | icon-kongtiao4 | 0 |  | {"monitor":"istatus,状态,,;s_fj,风机,4,;s_zl,制冷状态,4,;s_jrq,加热器,4,;s_jsq,加湿器 ,4,;s_csj,除湿器,4,;r_tem,回风温度,0,;r_hum,回风湿度,0,%RH;temset,设定温度,0,℃;humset,设定湿度,0,%RH","figure":",istatus,,;,s_fj,,;,s_zl,,;,s_jrq,,;,s_jsq,,;,s_csj,,;dial3,r_tem,,;dial3,r_hum,,%RH;dial3,temset,,℃;dial3,humset,,%RH","exhibition":"istatus,状态,;r_tem,回风温度,;r_hum,回风湿度,%RH;temset,设定温度,℃;humset,设定湿度,%RH","briefing":"istatus,状态,;r_tem,回风温度,;r_hum,回风湿度,%RH;temset,设定温度,℃;humset,设定湿度,%RH","history":"r_tem,回风温度,;r_hum,回风湿度,%RH;temset,设定温度,℃;humset,设定湿度,%RH","coefficient":"r_tem,0.1;r_hum,1;temset,0.1;humset,1","re_s_fj":"0,关闭;1,开启","re_s_zl":"0,关闭;1,开启","re_s_jrq":"0,关闭;1,开启","re_s_jsq":"0,关闭;1,开启","re_s_csj":"0,关闭;1,开启"} | 0
空调控制器-新版 | 4944 | icon-kongtiao4 | 1 | cmdid;电源;radiogroup;制冷开机;制冷开机,制热开机,关机;null cold;制冷温度;processbar;18;18,27;℃;null hot;制热温度;processbar;18;18,27;℃;null | {"monitor":"istatus,状态,,;V40001,当前湿度,,%;V40002,当前温度,,°C","figure":",istatus,,;dial3,V40001,,%;dial3,V40002,,°C","exhibition":"V40001,当前湿度,%;V40002,当前温度,°C","briefing":"V40001,当前湿度,%;V40002,当前温度,°C","chart":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,°C","coefficient":"V40001,0.1;V40002,0.1"} | 0
温湿度传感器（旧款） | 1280 | icon-dial2 | 0 |  | {"tn_field":"Tem","as_time":"08:00~08:05","monitor":"istatus,温湿度状态,,;Tem,温度,4,℃;Hum,湿度,0,%","figure":",istatus,,;dial3,Tem,,℃;dial3,Hum,,%","exhibition":"istatus,温湿度状态,;Tem,温度,℃;Hum,湿度,%","briefing":"Tem,温度,℃;Hum,湿度,%","chart":"Tem,温度,℃;Hum,湿度,%","history":"Tem,温度,℃;Hum,湿度,%","coefficient":"Tem,0.1;Hum,0.1"} | 0
电池检测 | 1044 | icon-ec2 | 0 |  | {"bar_0":"Vot;电压;1;32;#e6e10e","bar_1":"Reg;内阻;1;32;#34d417","bar_2":"Tem;温度;1;32;#21d9f3"} | 16
未命名的设备类型 | 2304 |  | 0 |  |  | 3
精密空调 | 4942 | icon-kongtiao3 | 0 |  | {"monitor":"istatus,空调状态,,;V110029,室内风机开关,,;V110030,压缩机1开关,,;V110031,压缩机2开关,,;V110032,电热器1开关,,;V110033,电热器2开关,,;V110034,加湿器开关,,;V110056,制冷开关,,;V110057,加热开关,,;V110058,加湿开关,,;V110059,除湿开关,,;V110081,漏水状态,4,;V110082,高温状态,4,;V110083,低温状态,4,;V110084,高湿状态,4,;V110085,低湿状态,4,;V110086,压缩机1高压状态,4,;V110087,压缩机1高压锁定状态,4,;V110088,压缩机2高压状态,4,;V110089,压缩机2高压锁定状态,4,;V110090,压缩机1低压状态,4,;V110091,压缩机1低压锁定状态,4,;V110092,压缩机2低压状态,4,;V110093,压缩机2低压锁定状态,4,;V110094,压缩机1排气状态,4,;V110096,压缩机2排气状态,4,;V110097,压缩机2排气锁定状态,4,;V110098,室内风机状态,4,;V110100,气流丢失状态,4,;V110101,滤网脏堵状态,4,;V110102,加湿器状态,4,;V110103,电加热器状态,4,;V110104,送风湿感状态,4,;V110105,送风温感状态,4,;V110106,回风温感状态,4,;V110107,回风湿感状态,4,;V110108,系统1出口温感状态,4,;V110109,系统2出口温感状态,4,;V110110,系统1低压压力传感状态,4,;V110111,系统2低压压力传感状态,4,;V110118,送风压感状态,4,;V110134,烟火状态,4,;V110136,电源,4,;V110137,组网状态,4,;V110138,室内机与室外机通讯状态,4,;V110139,系统1高压压力传感器状态,4,;V110141,系统2高压压力传感器状态,4,;V110145,室外温感状态,4,;V110150,加湿水阀状态,4,;V110156,加湿运行时间状态,4,","figure":",istatus,,;,V110029,,;,V110030,,;,V110031,,;,V110032,,;,V110033,,;,V110034,,;,V110056,,;,V110057,,;,V110058,,;,V110059,,;,V110081,,;,V110082,,;,V110083,,;,V110084,,;,V110085,,;,V110086,,;,V110087,,;,V110088,,;,V110089,,;,V110090,,;,V110091,,;,V110092,,;,V110093,,;,V110094,,;,V110096,,;,V110097,,;,V110098,,;,V110100,,;,V110101,,;,V110102,,;,V110103,,;,V110104,,;,V110105,,;,V110106,,;,V110107,,;,V110108,,;,V110109,,;,V110110,,;,V110111,,;,V110118,,;,V110134,,;,V110136,,;,V110137,,;,V110138,,;,V110139,,;,V110141,,;,V110145,,;,V110150,,;,V110156,,","re_V110029":"0,关;1,开","re_V110030":"0,关;1,开","re_V110031":"0,关;1,开","re_V110032":"0,关;1,开","re_V110033":"0,关;1,开","re_V110034":"0,关;1,开","re_V110056":"0,关;1,开","re_V110057":"0,关;1,开","re_V110058":"0,关;1,开","re_V110059":"0,关;1,开","re_V110081":"0,正常;1,告警","re_V110082":"0,正常;1,告警","re_V110083":"0,正常;1,告警","re_V110084":"0,正常;1,告警","re_V110085":"0,正常;1,告警","re_V110086":"0,正常;1,告警","re_V110087":"0,正常;1,告警","re_V110088":"0,正常;1,告警","re_V110089":"0,正常;1,告警","re_V110090":"0,正常;1,告警","re_V110091":"0,正常;1,告警","re_V110092":"0,正常;1,告警","re_V110093":"0,正常;1,告警","re_V110094":"0,正常;1,告警","re_V110096":"0,正常;1,告警","re_V110097":"0,正常;1,告警","re_V110098":"0,正常;1,告警","re_V110100":"0,正常;1,告警","re_V110101":"0,正常;1,告警","re_V110102":"0,正常;1,告警","re_V110103":"0,正常;1,告警","re_V110104":"0,正常;1,告警","re_V110105":"0,正常;1,告警","re_V110106":"0,正常;1,告警","re_V110107":"0,正常;1,告警","re_V110108":"0,正常;1,告警","re_V110109":"0,正常;1,告警","re_V110110":"0,正常;1,告警","re_V110111":"0,正常;1,告警","re_V110118":"0,正常;1,告警","re_V110134":"0,正常;1,告警","re_V110136":"0,正常 ;1,告警","re_V110137":"0,正常;1,告警","re_V110138":"0,正常;1,告警","re_V110139":"0,正常;1,告警","re_V110141":"0,正常;1,告警","re_V110145":"0,正常;1,告警","re_V110150":"0,正常;1,告警","re_V110156":"0,正常;1,告警"} | 0
UPS | 791 | icon-kongtiao4 | 0 |  | {"monitor":"b0,电池自检,,;b1,电池充电,,;b10,旁路晶闸管故障,,;b11,熔丝断,,;b12,母线电压异常,,;b13,初始化故障,,;b14,电池晶闸管故障,,;b15,充电器故障,,;b2,整流器状态,,;b3,整流器限流,,;b4,整流器故障,,;b5,逆变器故障,,;b6,辅助电源故障,,;b7,风扇故障,,;b8,输入晶闸管故障,,;b9,逆变晶闸管故障,,;Fin1,输入频率A,,Hz;Fin2,输入频率B,,Hz;Fin3,输入频率C,,Hz;Fout1,输出频率A,,Hz;Fout2,输出频率B,,Hz;Fout3,输出频率C,,Hz;Iin1,输入电流A,0,A;Iin2,输入电流B,0,A;Iin3,输入电流C,0,A;Iout1,输出电流A,0,A;Iout2,输出电流B,0,A;Iout3,输出电流C,0,A;istatus,UPS状态,,;Mbatt,电池剩余时间,,min;Pbatt,电池容量,,%;VB1,旁路电压A,0,V;VB2,旁路电压B,0,V;VB3,旁路电压C,0,V;Vbatt,电池电压,0,V;Vin1,输入电压A,0,V;Vin2,输入电压B,0,V;Vin3,输入电压C,0,V;Vout1,输出电压A,0,V;Vout2,输出电压B,0,V;Vout3,输出电压C,0,V","figure":",b0,,;,b1,,;,b10,,;,b11,,;,b12,,;,b13,,;,b14,,;,b15,,;,b2,,;,b3,,;,b4,,;,b5,,;,b6,,;,b7,,;,b8,,;,b9,,;,Fin1,,Hz;,Fin2,,Hz;,Fin3,,Hz;,Fout1,,Hz;,Fout2,,Hz;,Fout3,,Hz;,Iin1,,A;,Iin2,,A;,Iin3,,A;,Iout1,,A;,Iout2,,A;,Iout3,,A;,istatus,,;,Mbatt,,min;,Pbatt,,%;,VB1,,V;,VB2,,V;,VB3,,V;,Vbatt,,V;meter,Vin1,300,V;meter,Vin2,300,V;meter,Vin3,300,V;,Vout1,,V;,Vout2,,V;,Vout3,,V","exhibition":"istatus,UPS状态,","coefficient":"Fin1,0.1;Fin2,0.1;Fin3,0.1;Fout1,0.1;Fout2,0.1;Fout3,0.1;Iin1,0.1;Iin2,0.1;Iin3,0.1;Iout1,0.1;Iout2,0.1;Iout3,0.1;Mbatt,0.1;Pbatt,0.1;VB1,0.1;VB2,0.1;VB3,0.1;Vbatt,0.1;Vin1,0.1;Vin2,0.1;Vin3,0.1;Vout1,0.1;Vout2,0.1;Vout3,0.1","re_b0":"1,电池自检中;0,正常","re_b1":"1,充电中;0,未充电","re_b10":"0,正常;1,告警","re_b11":"0,正常;1,告警","re_b12":"0,正常;1,告警","re_b13":"0,正常;1,告警","re_b14":"0,正常;1,告警","re_b15":"0,正常;1,告警","re_b2":"0,停止;1,工作","re_b3":"0,未工作;1,工作中","re_b4":"0,正常;1,告警","re_b5":"0,正常;1,告警","re_b6":"0,正常;1,告警","re_b7":"0,正常;1,告警","re_b8":"0,正常;1,告警","re_b9":"0,正常;1,告警"} | 0