Protocol in P38	2

1.	Warning item	2

2. Capability setting（look for Application example 1）	3

3. Support Capability list	4

4. Control item（look for Application example 2）	4

5. The result of control	5

6. Setting Parameter to default value	5

7. UPS working status	5

8. UPS  battery information (sys or rack info inquiry addr)	6

9.The temperature inquiry	7

10. The three phase load inquiry	7

11. Load level inquiry	7

12. The bypass three phase info	7

14. UPS working Mode	8

15. UPS fault information	8

16. Loss point	8

19. Setting Parameter succeed or fail	8

20. Remote shutdown and test	9

21. CPU information	9

22. UPS model and rating information	9

Note	10

1. Note1	10

2. Note2	10

3. Note3	11

Application example	13

1. Audible alarm Enable or Disable	13

2. Setting buzzer beeps Silent.	13

3. Setting control parameter to default value	13

4. Get input voltage	13

5. Output socket status	13

6. Remote shut down the UPS	14

7. Shut down UPS and auto restart later	14

8. Setting Parameter item	14

：unused

- Protocol in P38

- Warning item

| Hex | Dec | Size | Content | Bit value | type |
| --- | --- | --- | --- | --- | --- |
| 0x0000 | 0 | bit15 | Battery open | 0:FALSE/1:TRUE | Read only |
|  |  | bit14 | IP N loss | 0:FALSE/1:TRUE | Read only |
|  |  | bit13 | IP site fail | 0:FALSE/1:TRUE | Read only |
|  |  | bit12 | Line phase error | 0:FALSE/1:TRUE | Read only |
|  |  | bit11 | Bypass phase error | 0:FALSE/1:TRUE | Read only |
|  |  | bit10 | Bypass frequency unstable | 0:FALSE/1:TRUE | Read only |
|  |  | bit9 | Battery over charge | 0:FALSE/1:TRUE | Read only |
|  |  | bit8 | Battery low | 0:FALSE/1:TRUE | Read only |
|  |  | bit7 | Overload warning | 0:FALSE/1:TRUE | Read only |
|  |  | bit6 | Fan lock warning | 0:FALSE/1:TRUE | Read only |
|  |  | bit5 | EPO active | 0:FALSE/1:TRUE | Read only |
|  |  | bit4 | Turn on abnormal | 0:FALSE/1:TRUE | Read only |
|  |  | bit3 | Over temperature | 0:FALSE/1:TRUE | Read only |
|  |  | bit2 | CHGFail | 0:FALSE/1:TRUE | Read only |
|  |  | bit1 | Remote shut down | 0:FALSE/1:TRUE | Read only |
|  |  | bit0 | L1 IP fuse fail | 0:FALSE/1:TRUE | Read only |
| 0x0001 | 1 | bit15 | L2 IP fuse fail | 0:FALSE/1:TRUE | Read only |
|  |  | bit14 | L3 IP fuse fail | 0:FALSE/1:TRUE | Read only |
|  |  | bit13 | L1 PFC positive error | 0:FALSE/1:TRUE | Read only |
|  |  | bit12 | L1 PFC negative error | 0:FALSE/1:TRUE | Read only |
|  |  | bit11 | L2 PFC positive error | 0:FALSE/1:TRUE | Read only |
|  |  | bit10 | L2 PFC negative error | 0:FALSE/1:TRUE | Read only |
|  |  | bit9 | L3 PFC positive error | 0:FALSE/1:TRUE | Read only |
|  |  | bit8 | L3 PFC negative error | 0:FALSE/1:TRUE | Read only |
|  |  | bit7 | CAN communication error | 0:FALSE/1:TRUE | Read only |
|  |  | bit6 | Synchronization line error | 0:FALSE/1:TRUE | Read only |
|  |  | bit5 | Synchronization pulse error | 0:FALSE/1:TRUE | Read only |
|  |  | bit4 | Host line error | 0:FALSE/1:TRUE | Read only |
|  |  | bit3 | Male connection error | 0:FALSE/1:TRUE | Read only |
|  |  | bit2 | Female connection error | 0:FALSE/1:TRUE | Read only |
|  |  | bit1 | Parallel line connection error | 0:FALSE/1:TRUE | Read only |
|  |  | bit0 | Battery connect different | 0:FALSE/1:TRUE | Read only |
| 0x0002 | 2 | bit15 | Line connect different | 0:FALSE/1:TRUE | Read only |
|  |  | bit14 | Bypass connect different | 0:FALSE/1:TRUE | Read only |
|  |  | bit13 | Mode type different | 0:FALSE/1:TRUE | Read only |
|  |  | bit12 | Parallel inverter voltage setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit11 | Parallel output frequency setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit10 | Battery cell over charge | 0:FALSE/1:TRUE | Read only |
|  |  | bit9 | Parallel output parallel setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit8 | Parallel output phase setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit7 | Parallel Bypass Forbidden setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit6 | Parallel Converter Enable setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit5 | Parallel Bypass Freq High loss setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit4 | Parallel Bypass Freq Low loss setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit3 | Parallel Bypass Volt High loss setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit2 | Parallel Bypass Volt Low Loss setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit1 | Parallel Line Freq High Loss setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit0 | Parallel Line Freq Low Loss setting different | 0:FALSE/1:TRUE | Read only |
| 0x0003 | 3 | bit15 | Parallel Line Volt High Loss setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit14 | Parallel Line Volt Low Loss setting different | 0:FALSE/1:TRUE | Read only |
|  |  | bit13 | Locked in bypass after overload 3 times in 30min | 0:FALSE/1:TRUE | Read only |
|  |  | bit12 | Warning for three-phase AC input current unbalance | 0:FALSE/1:TRUE | Read only |
|  |  | bit11 | Battery Phase loss | 0:FALSE/1:TRUE | Read only |
|  |  | bit10 | Inverter current unbalance | 0:FALSE/1:TRUE | Read only |
|  |  | bit9 | P1 cut off pre-alarm | 0:FALSE/1:TRUE | Read only |
|  |  | bit8 | Warning for Battery replace | 0:FALSE/1:TRUE | Read only |
|  |  | bit7 | Warning for input phase error | 0:FALSE/1:TRUE | Read only |
|  |  | bit6 | Cover of maintain switch is open | 0:FALSE/1:TRUE | Read only |
|  |  | bit5 | Phase Auto Adapt Failed | 0:FALSE/1:TRUE | Read only |
|  |  | bit4 | Utility extremely unbalanced | 0:FALSE/1:TRUE | Read only |
|  |  | bit3 | Bypass unstable | 0:FALSE/1:TRUE | Read only |
|  |  | bit2 | Parallel protect warning | 0:FALSE/1:TRUE | Read only |
|  |  | bit1 | Discharger overly | 0:FALSE/1:TRUE | Read only |
|  |  | bit0 | Battery too high | 0:FALSE/1:TRUE | Read only |
| 0x0004 | 4 | bit15 | Battery too low | 0:FALSE/1:TRUE | Read only |
|  |  | bit14 | Battery Volt High | 0:FALSE/1:TRUE | Read only |
|  |  | bit13 | Battery Volt Unbalance | 0:FALSE/1:TRUE | Read only |
|  |  | bit12 | CHG Short | 0:FALSE/1:TRUE | Read only |

- 2. Capability setting（look for Application example 1）

| Hex | Dec | Size | Content | Bit value | Register value | type |
| --- | --- | --- | --- | --- | --- | --- |
| 0x00 06 | 6 | bit15 | Enable/disable audible alarm | 0:FALSE/1:TRUE | E:8000/D:7FFF | Read/Write |
|  |  | bit14 | Enable/disable battery mode audible warning | 0:FALSE/1:TRUE | E:4000/D:BFFF | Read/Write |
|  |  | bit13 | Enable/disable battery open status check | 0:FALSE/1:TRUE | E:2000/D:DFFF | Read/Write |
|  |  | bit12 | Enable/disable high efficiency mode（ECO mode） | 0:FALSE/1:TRUE | E:1000/D:EFFF | Read/Write |
|  |  | bit11 | Enable/disable bypass forbidden | 0:FALSE/1:TRUE | E:800/D:F7FF | Read/Write |
|  |  | bit10 | Enable/disable inverter short clear function | 0:FALSE/1:TRUE | E:400/D:FBFF | Read/Write |
|  |  | bit9 | Enable/disable bypass when UPS turn off.（bps enable/disable） | 0:FALSE/1:TRUE | E:200/D:FDFF | Read/Write |
|  |  | bit8 | Enable/disable bypass audible warning | 0:FALSE/1:TRUE | E:100/D:FEFF | Read/Write |
|  |  | bit7 | Enable/disable auto-restart | 0:FALSE/1:TRUE | E:80/D:FF7F | Read/Write |
|  |  | bit6 | Enable/disable battery deep discharge protect | 0:FALSE/1:TRUE | E:40/D:FFBF | Read/Write |
|  |  | bit5 | Enable/disable battery low protect (if disable, the battery will discharge to 6V) | 0:FALSE/1:TRUE | E:20/D:FFDF | Read/Write |
|  |  | bit4 | Enable/disable converter mode | 0:FALSE/1:TRUE | E:10/D:FFEF | Read/Write |
|  |  | bit3 | Enable/disable period battery test | 0:FALSE/1:TRUE | E:8/D:FFF7 | Read/Write |
|  |  | bit2 |  | 0:FALSE/1:TRUE | E:4/D:FFFB | Read/Write |
|  |  | bit1 | Enable/disable battery test stop by time | 0:FALSE/1:TRUE | E:2/D:FFFD | Read/Write |
|  |  | bit0 | Enable/disable battery test stop by voltage |  | E:1/D:FFFE | Read/Write |
| 0x0007 | 7 | bit15 | Enable/disable frequency auto detection | 0:FALSE/1:TRUE | E:8000/D:7FFF | Read/Write |
|  |  | bit14 | Enable/disable auto bateery test function | 0:FALSE/1:TRUE | E:4000/D:BFFF | Read/Write |
|  |  | bit13 | Enable/disable waring mute | 0:FALSE/1:TRUE | E:2000/D:DFFF | Read/Write |
|  |  | bit12 | Enable/disable fault mute | 0:FALSE/1:TRUE | E:1000/D:EFFF | Read/Write |
|  |  | bit11 | Enable/disable all mode mute | 0:FALSE/1:TRUE | E:0800/D:F7FF | Read/Write |
|  |  |  | bit0 - b10 =Reservation |  |  |  |

- 3. Support Capability list

--

- 4. Control item（look for Application example 2）

| Hex | Dec | Size | Content | Bit value | Register value | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0x001A | 26 | bit15 | bit15=Silence buzzer beep | 0:FALSE/1:TRUE | Y:8000/N:7FFF | Read/Write |
|  |  | bit14 | bit14=buzzer beep open | 0:FALSE/1:TRUE | Y:4000/N:BFFF | Read/Write |
|  |  | bit13 | bit13=Test until battery low | 0:FALSE/1:TRUE | Y:2000/N:DFFF | Read/Write |
|  |  | bit12 | bit12=Remote turn off UPS | 0:FALSE/1:TRUE | Y:1000/N:EFFF | Read/Write |
|  |  | bit11 | bit11=Remote turn on UPS | 0:FALSE/1:TRUE | Y:800/N:F7FF | Read/Write |
|  |  | bit10 | bit10=Cancel shutdown | 0:FALSE/1:TRUE | Y:400/N:FBFF | Read/Write |
|  |  | bit9 | bit9=Cancel test | 0:FALSE/1:TRUE | Y:200/N:FDFF | Read/Write |
|  |  | bit8 | bit8=10 seconds test | 0:FALSE/1:TRUE | Y:100/N:FEFF | Read/Write |
|  |  | bit7 | bit7= Reservation |  |  |  |
|  |  | bit6 | bit6 = Reservation |  |  |  |
|  |  | bit5 | bit5= Reservation |  |  |  |
|  |  | bit4 | bit4 = Reservation |  |  |  |
|  |  |  | b3-b0 = Reservation |  |  |  |

- 5. The result of control

| Hex | Dec | Size | Content | Bit value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0025 | 37 | bit15 | bit15=Flag:Silence buzzer beep | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit14 | bit14=Flag:buzzer beep open | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit13 | bit13=Flag:Test until battery low | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit12 | bit12=Flag:Remote turn off UPS | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit11 | bit11=Flag:Remote turn on UPS | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit10 | bit10=Flag:Cancel shutdown | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit9 | bit9=Flag:Cancel test | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit8 | bit8=Flag:10 seconds test | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit7 | bit7= Reservation | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit6 | bit6 = Reservation | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit5 | bit5= Reservation | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit4 | bit4 = Reservation | 0:FAIL/1:SUCCESS | Read/Write |
|  |  |  | b3-b0 = Reservation | 0:FAIL/2:SUCCESS | Read/Write |

- 6. Setting Parameter to default value

| Hex | Dec | Size | Content | Bit value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0030 | 48 | bit15 | bit15=Seting control parameter to default value | 0:FAIL/1:SUCCESS | Read/Write |
|  |  |  | b14-b0 = Reservation |  |  |
| 0x003B | 59 | bit15 | bit15=Flag:Seting control parameter to default value | 0:FAIL/1:SUCCESS | Read |
|  |  |  | b14-b0 = Reservation |  |  |

- 7. UPS working status

| Hex | Dec | Size | Content | units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x031E | 798 | 1 | R Input voltage | 0.1V | Read only |
| 0x031F | 799 | 1 | S Input voltage | 0.1V | Read only |
| 0x0320 | 800 | 1 | T Input voltage | 0.1V | Read only |
| 0x0321 | 801 | 1 | Input frequency | 0.1Hz | Read only |
| 0x0322 | 802 | 1 | R Output voltage | 0.1V | Read only |
| 0x0323 | 803 | 1 | S Output voltage | 0.1V | Read only |
| 0x0324 | 804 | 1 | T Output voltage | 0.1V | Read only |
| 0x0325 | 805 | 1 | Output frequency | 0.1Hz | Read only |
| 0x0326 | 806 | 1 | R Output current | 0.1A | Read only |
| 0x0327 | 807 | 1 | S Output current | 0.1A | Read only |
| 0x0328 | 808 | 1 | T Output current | 0.1A | Read only |
| 0x0329 | 809 | 1 | R Output load percent | 0.1% | Read only |
| 0x032A | 810 | 1 | S Output load percent | 0.1% | Read only |
| 0x032B | 811 | 1 | T Output load percent | 0.1% | Read only |
| 0x00AF | 175 | 1 | Total Output load percent | 0.1% | Read only |
| 0x032C | 812 | 1 | P Battery voltage | 0.1V | Read only |
| 0x032D | 813 | 1 | N Battery voltage | 0.1V | Read only |
| 0x032E | 814 | 1 | Max Temperature of the detecting pointers | 0.1C | Read only |
| 0x032F | 815 | 1 | status | Note1 | Read only |

- 8. UPS  battery information (sys or rack info inquiry addr)

| 0x00BC | 188 | 1 | P Battery voltage | 0.1V | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x00BD | 189 | 1 | P Battery Charging Current |  | Read only |
| 0x00BE | 190 | 1 | P Battery Discharging Current | Ah | Read only |
| 0x00BF | 191 | 1 | Battery Capacity | % | Read only |
| 0x00C0 | 192 | 1 | Battery Remain time(minute) | minutes | Read only |
| 0x00C1 | 193 | 1 | N Battery voltage | 0.1V | Read only |
| 0x00C2 | 194 | 1 | N Battery Charging Current |  | Read only |
| 0x00C3 | 195 | 1 | N Battery Discharging Current | Ah | Read only |
| 0x00C4 | 196 | 1 | -- | % | Read only |
| 0x00C5 | 197 | 1 | -- | minutes | Read only |
| 0x02ED | 749 | 1 | Battery mode work time | min | Read only |
| 0x0307 | 775 | 1 | Battery AH Number | AH | Read only |
| 0x0318 | 792 | 1 | -- | 0.01A | Read only |
| 0x0319 | 793 | 1 | -- | 0.01A | Read only |
| 0x0364 | 868 | 1 | Battery shutdown voltage | 0.1V | Read/Write |
| 0x036A | 874 | 1 | Battery Low voltage | 0.1V | Read/Write |
| 0x048D | 1165 | 1 | battery cell number |  | Read only |
| 0x05B0 | 1456 | 1 | Battery High voltage | 0.1V | Read/Write |
| 0x05B1 | 1457 | 1 | Battery max charging current | 0.1A | Read only |
| 0x05D5 | 1493 | 1 | Battery Bluk voltage | 0.1V | Read only |

- 9.The temperature inquiry

| 0x00CC | 204 | 1 | heatsink temperature 1 | ℃ | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x00CD | 205 | 1 | heatsink temperature 2 | ℃ | Read only |
| 0x00CE | 206 | 1 | cabinet temperature | ℃ | Read only |
| 0x00CF | 207 | 1 | battery temperature | ℃ | Read only |

- 10. The three phase load inquiry

| 0x00DD | 221 | 1 | R phase of load | 0.1% | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x00FC | 252 | 1 | S phase of load | 0.1% | Read only |
| 0x00FD | 253 | 1 | T phase of load | 0.1% | Read only |
| 0x00FE | 254 | 1 | The whole load | 0.1% | Read only |

- 11. Load level inquiry

| 0x00B7 | 183 | 1 | Total Watt percent | 0.1% | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x00B8 | 184 | 1 | Total VA percent | 0.1% | Read only |
| 0x030C | 780 | 1 | Load VA R |  | Read only |
| 0x030D | 781 | 1 | Load VA S |  | Read only |
| 0x030E | 782 | 1 | Load VA T |  | Read only |
| 0x030F | 783 | 1 | Load Watt R |  | Read only |
| 0x0310 | 784 | 1 | Load Watt S |  | Read only |
| 0x0311 | 785 | 1 | Load Watt T |  | Read only |
| 0x0312 | 786 | 1 | R Watt percent | 0.1% | Read only |
| 0x0313 | 787 | 1 | S Watt percent | 0.1% | Read only |
| 0x0314 | 788 | 1 | T Watt percent | 0.1% | Read only |
| 0x0315 | 789 | 1 | R VA percent | 0.1% | Read only |
| 0x0316 | 790 | 1 | S VA percent | 0.1% | Read only |
| 0x0317 | 791 | 1 | T VA percent | 0.1% | Read only |

- 12. The bypass three phase info

| 0x011A | 282 | 1 | R voltage of bypass | 0.1V | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x011B | 283 | 1 | S voltage of bypass | 0.1V | Read only |
| 0x011C | 284 | 1 | T voltage of bypass | 0.1V | Read only |
| 0x011D | 285 | 1 | R current of bypass | 0.1A | Read only |
| 0x011E | 286 | 1 | S current of bypass | 0.1A | Read only |
| 0x011F | 287 | 1 | T current of bypass | 0.1A | Read only |
| 0x0123 | 291 | 1 | frequency of bypass | 0.1Hz | Read only |

- 14. UPS working Mode

| 0x00D0 | 208 | 1 | UPS Mode inquiry | Note2 | Read only |
| --- | --- | --- | --- | --- | --- |

- 15. UPS fault information

| 0x02A3 | 675 | 1 | Fault kind ASC | Note3 | Read only |
| --- | --- | --- | --- | --- | --- |

- 16. Loss point

| Hex | Dec | Size | Content | Units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x034A | 842 | 1 | Line Voltage High | V | Read only |
| 0x034B | 843 | 1 | Line Voltage Low | V | Read only |
| 0x034C | 844 | 1 | Line Frequency High | 0.1Hz | Read only |
| 0x034D | 845 | 1 | Line Frequency Low | 0.1Hz | Read only |
| 0x034E | 846 | 1 | Bypass Frequency High | V | Read/Write |
| 0x034F | 847 | 1 | Bypass Frequency Low | V | Read/Write |
| 0x0350 | 848 | 1 | Bypass Voltage High | 0.1Hz | Read/Write |
| 0x0351 | 849 | 1 | Bypass Voltage Low | 0.1Hz | Read/Write |
| 0x0352 | 850 | 1 | ECO Voltage High | V | Read/Write |
| 0x0353 | 851 | 1 | ECO Voltage Low | V | Read/Write |
| 0x0354 | 852 | 1 | ECO Frequency High | 0.1Hz | Read/Write |
| 0x0355 | 853 | 1 | ECO Frequency Low | 0.1Hz | Read/Write |

- 19. Setting Parameter succeed or fail

| Hex | Dec | Size | Content | Bit value | type |
| --- | --- | --- | --- | --- | --- |
| 0x0384 | 900 | Bit15 | Flag:Bypass Frequency High | 0:FALSE/1:TRUE | Read only |
|  |  | Bit14 | Flag:Bypass Frequency Low | 0:FALSE/1:TRUE | Read only |
|  |  | Bit13 | Flag:Bypass Voltage High | 0:FALSE/1:TRUE | Read only |
|  |  | Bit12 | Flag:Bypass Voltage Low | 0:FALSE/1:TRUE | Read only |
|  |  | Bit11 | Flag:ECO Voltage High | 0:FALSE/1:TRUE | Read only |
|  |  | Bit10 | Flag:ECO Voltage Low | 0:FALSE/1:TRUE | Read only |
|  |  | Bit9 | Flag:ECO Frequency High | 0:FALSE/1:TRUE | Read only |
|  |  | Bit8 | Flag:ECO Frequency Low | 0:FALSE/1:TRUE | Read only |
|  |  | Bit7 | Flag: Battery shutdown voltage | 0:FALSE/1:TRUE | Read only |
|  |  | Bit6 | Flag: Battery Low voltage | 0:FALSE/1:TRUE | Read only |
|  |  | Bit5 | Flag: Battery High voltage | 0:FALSE/1:TRUE | Read only |

- 20. Remote shutdown and test

| Hex | Dec | Size | Content | Units/Bit value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x03AB | 939 | 1 | Shutdown | minutes(ASCII) | Read/Write |
| 0x03AC | 940 | 1 | Test for specified time | minutes(ASCII) | Read/Write |
| 0x03AD | 941 | 1 | Shutdown and restore(N) | minutes(ASCII) | Read/Write |
| 0x03AE | 942 | 2 | Shutdown and restore(M) | minutes(ASCII) | Read/Write |
| 0x03DA | 986 | bit15 | B15=flag:Shutdown | 0:FAIL/1:SUCCESS | Read only |
|  |  | bit14 | B14=flag:Test for specified time | 0:FAIL/1:SUCCESS | Read only |
|  |  | bit13 | B13=flag:Shutdown and restore | 0:FAIL/1:SUCCESS | Read only |
|  |  |  | b12-b0=Reservation |  |  |

- 21. CPU information

| Hex | Dec | Size | Content | Units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x03E0 | 992 | 1 | Protocol ID Inquiry | ASCII | Read only |
| 0x03E1 | 993 | 10 | Main CPU Firmware version | ASCII | Read only |

- 22. UPS model and rating information

| 0x03EB | 1003 | 7 | Main Production type | ASCII | Read only |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Sub Production type | ASCII | Read only |
|  |  |  | VA type | ASCII | Read only |
|  |  |  | H/LV type | ASCII | Read only |
|  |  |  | Year | ASCII | Read only |
|  |  |  | Month | ASCII | Read only |
|  |  |  | Manufacturer ID | ASCII | Read only |
|  |  |  | Serial number | ASCII | Read only |
| 0x03F2 | 1010 | 1 | Battery Piece Number |  | Read only |
| 0x03F3 | 1011 | 1 | Battery standard voltage per unit | 0.1V | Read only |
| 0x03F4 | 1012 | 1 | Input phase |  | Read only |
| 0x03F5 | 1013 | 1 | Output phase |  | Read only |
| 0x03F6 | 1014 | 1 | Nominal I/P Voltage | V | Read only |
| 0x03F7 | 1015 | 1 | Nominal O/P Voltage | V | Read only |
| 0x03F8 | 1016 | 1 | Output power factor |  | Read only |
| 0x03F9 | 1017 | 2 | Output rated VA | W | Read only |
| 0x03FB | 1019 | 8 | Device model | ASCII | Read only |
| 0x048A | 1162 | 1 | Battery Voltage | 0.1V | Read only |
| 0x048B | 1163 | 1 | Rating Output Current | 0.1A | Read only |
| 0x048C | 1164 | 1 | Rating Output Frequency | 0.1Hz | Read/Write |
| 0x048D | 1165 | 1 | Rating Output Voltage | 0.1V | Read/Write |
| 0x048E | 1166 | 1 | The parallel number. |  | Read only |

- Note

# 1. Note1

| Note 1: |  |
| --- | --- |
| 815（bit15-bit8） | bit15 bit14： 00: standy; 01: line-interactive; 10: on-line. |
|  | bit13: Utility Fail bit12: Battery Low bit11: Bypass/Boost Active bit10: UPS Failed bit9: EPO bit8: Test in Progress |
| 815 （bit2-bit0） | Bit2: Shutdown Active bit1: bat silence bit0: Bat test OK |

# 2. Note2

| Note 2: |  |  |
| --- | --- | --- |
| 0x00D0H | P: | Power on mode |
|  | S: | Standby mode |
|  | Y: | Bypass mode |
|  | L: | Line mode |
|  | B: | Battery mode |
|  | T: | Battery test mode |
|  | F: | Fault mode |
|  | E: | HE/ECO mode |
|  | C: | Converter mode |
|  | D: | Shutdown mode |

# 3. Note3

| Fault Kind | Fault Number | Fault Name |
| --- | --- | --- |
| Bus fault | 0x01 | Bus start fail |
|  | 0x02 | Bus volt over |
|  | 0x03 | Bus volt under |
|  | 0x04 | Bus volt unbalance |
|  | 0x05 | Bus short |
|  | 0x06 | PFC over current |
|  | 0x07 | PFC IGBT over current |
|  | 0x08 | Input contact fault |
| Inverter fault | 0x11 | Inverter soft fail |
|  | 0x12 | Inverter volt high |
|  | 0x13 | Inverter volt low |
|  | 0x14 | L1 inverter short |
|  | 0x15 | L2 inverter short |
|  | 0x16 | L3 inverter short |
|  | 0x17 | L1L2 inverter short |
|  | 0x18 | L2L3 inverter short |
|  | 0x19 | L3L1 inverter short |
|  | 0x1A | L1 inverter negative power |
|  | 0x1B | L2 inverter negative power |
|  | 0x1C | L3 inverter negative power |
| Electric link fault | 0x21 | Bat SCR short fault |
|  | 0x22 | Line SCR short fault |
|  | 0x23 | Inverter relay open fault |
|  | 0x24 | Inverter relay short fault |
|  | 0x25 | Wiring fault |
|  | 0x26 | Battery reverse fault |
|  | 0x27 | Battery too high |
|  | 0x28 | Battery too low |
|  | 0x29 | Battery Fuse |
|  | 0x30 | Open-Circuit Fault |
| Parallel system fault | 0x31 | CAN communication fault |
|  | 0x32 | Host line fault |
|  | 0x33 | Synchronization line fault |
|  | 0x34 | Synchronization pulse line fault |
|  | 0x35 | Parallel communication line loss |
|  | 0x36 | Output circuit fault |
| Others | 0x41 | Over temperature |
|  | 0x42 | CPU communication fault |
|  | 0x43 | Overload fault |
|  | 0x44 | Fan fault |
|  | 0x45 | Charger fault |
|  | 0x46 | Model fault |
|  | 0x47 | MCU communication fault |
|  | 0x48 | DSP firmware version incompatible |
|  | 0x49 | IpOPPhaseError |
|  | 0x4A |  |
|  | 0x4B |  |
|  | 0x4C |  |
|  | 0x4D |  |
|  | 0x4E |  |
|  | 0x4F |  |
|  | 0x60 | Inverter over current |
|  | 0x61 | BypScrShort |
|  | 0x62 | BypScrOpen |
|  | 0x63 | RINVWaveAbnormal |
|  | 0x64 | SINVWaveAbnormal |
|  | 0x65 | TINVWaveAbnormal |
|  | 0x66 | CTSatiation |
|  | 0x67 | OPShort_BYP |
|  | 0x68 | OPLineShort_BYP |
|  | 0x69 | InvScrShort |
|  | 0x6A | BusVoltVaryFault |

- Application example

- 1. Audible alarm Enable or Disable

Look for Enable audible alarm, It in table address 0x000E bit15.Then you may write 0x8000 to 0x000E to Enable audible alarm or write 0xEFFF to 0x0E to disable audible alarm.

For example:

[XX 10 00 0E 00 01 02 80 00 CRCL CRCH]Mean: Enable audible alarm.

[XX 10 00 0E 00 01 02 7F FF CRCL CRCH]Mean: Disable audible alarm.

Inquire the result of execute, you may read the follow address 0x10 bit15.

For example:

[XX 03 00 10 00 01 CRCL CRCH]

[XX 03 02 80 00 CRCL CRCH]Mean: Execute success

[XX 03 02 00 00 CRCL CRCH]Mean: Execute fail

- 2. Setting buzzer beeps Silent.

Look for silence buzzer beep in address 0x001A  bit 15 。Then you may write 0x8000 to 0x001A.

For example:

[XX 10 00 1A 00 01 02 80 00 CRCL CRCH]Silence buzzer beep.

Inquire the execution result. You may read 0x0025

[XX 03 00 25 00 01 CRCL CRCH] to inquire the results of command.

- 3. Setting control parameter to default value

Look for setting control parameter to default value it ,then write 0x8000 to 0x0030.If execute success then set 0x003B bit15 to 1;

For example:

[XX 10 00 30 00 01 02 80 00 CRCL CRCH]Setting control parameter to default value.

[XX 03 00 3B 00 01 CRCL CRCH]to inquire the results of command.

- 4. Get input voltage

Look for input voltage in address 0x00AA, when read 0x00AA to get input voltage and it units is 0.1V

For example:

PC:[XX 03 00 AA 00 01 CRCL CRH]

DEVICE:[XX 03 02 08 89 CRCL CRCH]

Mean: HEX [0x0889] to DEC[2185] .Input voltage:218.5V.

- 5. Output socket status

Inquire output socket status, Write socket number to 0x0345,then read 0x0346 to inquire socket status.

For example:

PC:[XX 10 03 45 00 01 02 01 00 CRCL CRCH] 01:Means inquire socket 1 status.

PC:[XX 03 03 46 00 01 CRCL CRCH]

DEVICE:[XX 03 02 01 00 CRCL CRCH]  01:Means socket1 was on.

- 6. Remote shut down the UPS

Remote shut down the UPS, then write is a number ranging from (.2, .3, ..., 01, 02,..., to 10)to the 0x3AB.If execute success then 0x003DA bit0 was set to 1.

For example:

PC:[XX 10 03 AB 00 01 02 2E 32]Mean: Shut down the UPS in 0.2 minutes

- 7. Shut down UPS and auto restart later

Cut UPS output off in <n> minutes and waiting for <m> minutes and then turn on UPS output again. Then write n to 0x03AD and write m to 0x003AE.

For example:

PC:[XX 10 03 AD 00 03 06 2E 32 30 30 30 32 CRCL CRCH]Mean: Shut down the UPS in 0.2 minutes and waiting

for 0002 minutes turn on the UPS.

- 8. Setting Parameter item

Set The bypass Voltage high loss point of UPS ,You want to Set the value 286V . Then write 0x011E to 0x0350 .

For example:

PC:[XX 10 03 50 00 01 02 01 1E CRCL CRCH]Mean: Set The bypass Voltage high loss point of UPS for 286V.