## Normal Command
SEC Command Format
^TnnnXXXX,XXXX,XXXX,,<CRC><cr>
Character | Description | Remark
^ | Start bit
T | Type | P: PC Query command, S: Set command, D: Device Response
nnn | Data length | Include CRC and ending character, except"^Tnnn"
XXXXX | Data | If the data is reserved, they will be filled nothing, so you would see double "," connected.
, | Seperator | Separate each data, please use "," to recognize the length of data. If double "," continuing, that means this data is reserved.
<CRC> | Two byte of CRC result, the first byte is high 8 bits, second byte is low 8 bits.
Query commands
^P006QPI<CRC><cr>: Query protocol ID
Response: ^D00540<CRC><cr>
^P007QGS1<CRC><cr>: Query general status
Response:^D130AAA.A,BBB.B,CCC.C,DD.D,EEE.E,FFF.F,GGG.G,HHH.H,III.I,JJJ.J,KK.K,LLL.L,MMM.M,NNN.N,OO.O,PPP.P,QQQ.Q,RRR.R,SSS.S,TT.T,UUU.U,VVV.V<CRC><cr>
Data | Description | Remark
AAA.A | Grid voltage(R) | A: 0~9, unit: 1V
BBB.B | Grid voltage(S) | B: 0~9, unit: 1V
CCC.C | Grid voltage(T) | C: 0~9, unit: 1V
DD.D | Grid frequency | D: 0~9, unit: 1Hz
EEE.E | Inverter voltage(R) | E: 0~9, unit: 1V
FFF.F | Inverter voltage(S) | F: 0~9, unit: 1V
GGG.G | Inverter voltage(T) | G: 0~9, unit: 1V
HHH.H | Inverter current(R) | H: 0~9, unit: 1A
III.I | Inverter current(S) | I: 0~9, unit: 1A
JJJ.J | Inverter current(T) | J: 0~9, unit: 1A
KK.K | Inverter frequency | K: 0~9, unit: 1Hz
LLL.L | Output voltage(R) | L: 0~9, unit: 1V
MMM.M | Output voltage(S) | M: 0~9, unit: 1V
NNN.N | Output voltage(T) | N: 0~9, unit: 1V
OO.O | Output frequency | O: 0~9, unit: 1Hz
PPP.P | Output current(R) | P: 0~9, unit: 1A
QQQ.Q | Output current(S) | Q: 0~9, unit: 1A
RRR.R | Output current(T) | R: 0~9, unit: 1A
SSS.S | Bypass voltage(R) | S: 0~9, unit: 1V
TT.T | Bypass frequency | T: 0~9, unit: 1Hz
UUU.U | Bypass voltage(S) | U: 0~9, unit: 1V
VVV.V | Bypass voltage(T) | V: 0~9, unit: 1V
^P007QGS2<CRC><cr>: Query general status
Response:^D120AA,BBB.B,CCC.C,DDD.D,EEE.E,FFF.F,GGG.G,HHHHH,IIIII,JJJJJ,KKKKK,LLLLL,MMMMM,NNN,OOO,PPP,QQQ,RRR.R,SSS.S,TT.T,UU.U,VV.V<CRC><cr>
Data | Description | Remark
AA | Working mode | A:0~9, 01[Poweron mode];02[Standby mode];03[Grid mode];04[Bypass mode];05[Battery mode];06[ECO mode];07[Fault mode];08[Shutdown mode];09[Test mode]
BBB.B | Grid voltage(RS) | B: 0~9, unit: 1V
CCC.C | Grid voltage(ST) | C: 0~9, unit: 1V
DDD.D | Grid voltage(TR) | D: 0~9, unit: 1V
EEE.E | Inverter voltage(RS) | E: 0~9, unit: 1V
FFF.F | Inverter voltage(ST) | F: 0~9, unit: 1V
GGG.G | Inverter voltage(TR) | G: 0~9, unit: 1V
HHHHH | AC output active power(R) | H: 0~9, unit: W
IIIII | AC output active power(S) | I: 0~9, unit: W
JJJJJ | AC output active power(T) | J: 0~9, unit: W
KKKKK | AC output apparent power® | K: 0~9, unit: VA
LLLLL | AC output apparent power(S) | L: 0~9, unit: VA
MMMMM | AC output apparent power(T) | M: 0~9, unit: VA
NNN | Output load percent(R) | N: 0~9, unit: %
OOO | Output load percent(S) | O: 0~9, unit: %
PPP | Output load percent(T) | P: 0~9, unit: %
QQQ | The max Output load percent | Q: 0~9, unit: %
RRR.R | Bus voltage | R: 0~9, unit: 1V
SSS.S | battery voltage | S: 0~9, unit: 1V
TT.T | Inverter DC component(R) | T: 0~9, unit: 1V
UU.U | Inverter DC component(S) | U: 0~9, unit: 1V
VV.V | Inverter DC component(T) | V: 0~9, unit: 1V
^P008PEPD?<CRC><cr>: Query enable/disable flag status
Response: ^D023Ax,Bx,Cx,Dx,Ex,Fx,Zx<CRC><cr>
Data | Description | Remark
x | 0 or 1
A | Enable/disable ECO mode | A: 0/1, 0: disable, 1: enable
B | Enable/Disable CVCF mode | B: 0/1, 0: disable, 1: enable
C | Enable/Disable Autorestart with battery | C: 0/1, 0: disable, 1: enable |  | auto restart
D | Enable/Disable Autorestart without battery | D: 0/1, 0: disable, 1: enable |  | no bat on load
E | Forbidden/Allow Bypass | E: 0/1, 0: allow, 1: forbidden
F | Enable/Disable auto to bypass | F: 0/1, 0: disable, 1: enable
Z | Reserve
notes | “C”表示接了电池时，电池低压机器掉电后，再次启动时自动进入逆变模式。 “D”表示只要没手动关过机，机器再次启动后自动进入逆变模式。
^P008SGVL?<CRC><cr>: Query grid voltage loss point
Response: ^D010AAA,BBB<CRC><cr>
Data | Description | Remark
AAA | High voltage point | A: 0~9, unit: 1V
BBB | Low voltage point | B: 0~9, unit: 1V
^P008SGFL?<CRC><cr>: Query grid frequency loss point
Response: ^D012AA.A,BB.B<CRC><cr>
Data | Description | Remark
AA.A | Frequency high loss | A: 0~9, unit: 1Hz
BB.B | Frequency Low loss | B: 0~9, unit: 1Hz
^P008SBVL?<CRC><cr>: Query bypass voltage loss point
Response: ^D010AAA,BBB<CRC><cr>
Data | Description | Remark
AAA | High voltage point | A: 0~9, unit: 1V
BBB | Low voltage point | B: 0~9, unit: 1V
^P008SBFL?<CRC><cr>: Query bypass frequency loss point
Response: ^D012AA.A,BB.B<CRC><cr>
Data | Description | Remark
AA.A | Frequency high loss | A: 0~9, unit: 1Hz
BB.B | Frequency Low loss | B: 0~9, unit: 1Hz
^P008SEVL?<CRC><cr>: Query ECO voltage loss point
Response: ^D010AAA,BBB<CRC><cr>
Data | Description | Remark
AAA | High voltage point | A: 0~9, unit: 1V
BBB | Low voltage point | B: 0~9, unit: 1V
^P008SEFL?<CRC><cr>: Query ECO frequency loss point
Response: ^D012AA.A,BB.B<CRC><cr>
Data | Description | Remark
AA.A | Frequency high loss | A: 0~9, unit: 1Hz
BB.B | Frequency Low loss | B: 0~9, unit: 1Hz
^P008BATN?<CRC><cr>: Query battery number
Response: ^D005AA<CRC><cr>
Data | Description | Remark
AA | The battery number | A: 0~9, unit: PCS
^P009QCHGMS<CRC><cr>: Query charging Settings
Response: ^D019AA.A,BB.B,CC,DDD<CRC><cr>
Data | Description | Remark
AA.A | The bulk voltage | A: 0~9, unit: 1V
BB.B | The floating voltage | B: 0~9, unit: 1V
CC | The charge current | C: 0~9, unit: 1A
DDD | The conversion time that constant voltage charging to floating | C: 0~9, unit: 1min
^P007OPV?<CRC><cr>: Query rated output voltage
Response: ^D006AAA<CRC><cr>
Data | Description | Remark
AAA | Rated output voltage | AAA:220 or 230 or 240, unit: 1V
^P007OPF?<CRC><cr>: Query rated output frequency
Response: ^D005AA<CRC><cr>
Data | Description | Remark
AA | Rated output frequency | AA:50 or 60 or 00, unit: 1Hz
^P008BCAP?<CRC><cr>: Query battery capacity
Response: ^D006AAA<CRC><cr>
Data | Description | Remark
AAA | Battery capacity | A:0~9, unit: 1Ah
^P008BGRP?<CRC><cr>: Query battery group
Response: ^D005AA<CRC><cr>
Data | Description | Remark
AA | Battery group | A:0~9, unit: 1group
^P008USID?<CRC><cr>: Query user ID
Response: ^DnnnAA,XXXXXXXXXXXXXXXXXXXXX<CRC><cr>
Data | Description | Remark
nnn | The available data length. | n:0~9, unit: 1
AA | The number of X, maximum is 21. | A:0~9, unit: 1
Example: ^D02014,01234567890123<CRC><cr>, it meas ID is 01234567890123.
^P007QVER<CRC><cr>: Query CPU version
Response: ^D020aaaaaaaa,bbbbbbbb<CRC><cr>
Data | Description | Remark
aaaaaaaa | Main CPU version
bbbbbbbb | Slave CPU version
^P008QPIWS<CRC><cr>: Query warning status
Response: ^D042ABCD,EFGH,IJKL,MNOP,QRST,UVWX,YZab,cdef<CRC><cr>
Data | Description | Remark
A~R | Reserve
S | The bypasses are inconsistent | 1 means abnormal，0 means normal
T | Maintenance bypass opens | 1 means abnormal，0 means normal
U | Reserve | 1 means abnormal，0 means normal
V | Reserve | 1 means abnormal，0 means normal
W | EEPEOM communication failed | 1 means abnormal，0 means normal
X | IO expansion card communication failed | 1 means abnormal，0 means normal
Y | The input frequency is unstable | 1 means abnormal，0 means normal
Z | Inverter over temperature | 1 means abnormal，0 means normal
a | EPO active | 1 means abnormal，0 means normal | 3006
b | Over load | 1 means abnormal，0 means normal | 5002
c | battery voltage low | 1 means abnormal，0 means normal | 3617
d | battery over charge | 1 means abnormal，0 means normal
e | input phase sequence errors | 1 means abnormal，0 means normal
f | battery open | 1 means abnormal，0 means normal | 4004
^P007QCHG<CRC><cr>: Query charging information
Response: ^D037AAA.A,BBB.B,CC.C,DDDDD,±EEE,FF,GGG<CRC><cr>
Data | Description | Remark
AAA.A | Real-time bus voltage | A: 0~9, unit: 1V
BBB.B | Real-time charging voltage | B: 0~9, unit: 1V
CC.C | Real-time charging current | C: 0~9, unit: 1A
DDDDD | Chager status | 0 means normal,otherwise it is an exception
±EEE | Chager temperature | E: 0~9, unit: 1℃
FF | Charging stage | FF: 00-bulk;01-Absorption;02-Float
GGG | Battery percentage | G: 0~9, unit: 1%
^P010QFAULTn<CRC><cr>: Query fault(n is the item that you want to query)
Response:^D116AA,BB,CCC,DDD,EEE,FF.F,GGG,HHH,III,JJJ,KKK,LLL,MM.M,NNN,OOO,PPP,QQQ,RRR,SSS,TTTTT,UUUUU,VVV,WWW,XXXXX,YYYYY,ZZZZZ<CRC><cr>
Data | Description | Remark
AA | Fault code | A: 0~9
B~Z | Fault information
故障码对应表
1 | 保留
2 | 保留
3 | 过载
4 | bus软起超时
5 | bus高压
6 | bus低压
7 | R相逆变短路
8 | S相逆变短路
9 | T相逆变短路
10 | R相逆变低压
11 | S相逆变低压
12 | T相逆变低压
13 | R相逆变高压
14 | S相逆变高压
15 | T相逆变高压
16 | RS逆变线电压短路
17 | ST逆变线电压短路
18 | TR逆变线电压短路
19 | 电池电压过高
20 | R相逆变过流
21 | S相逆变过流
22 | T相逆变过流
23 | IGBT过流
24 | 逆变软起超时
25 | R相IGBT过流
26 | S相IGBT过流
27 | T相IGBT过流
28 | 逆变电流零偏过大
29 | 输出电流零偏过大
30 | 逆变过温
31 | 变压器过温
32 | R相SCR短路
33 | S相SCR短路
34 | T相SCR短路
35 | CAN通讯失败
36 | 输出设置不同步
37 | 并机主机信号缺失
38 | 并机同步信号缺失
39 | 并机版本不正确
40 | 输出过温
^P007QSTU<CRC><cr>: Query work status
Response:^D032AA,BB,CC,DDDDD,EEEEE,FF,GG,HH<CRC><cr>
Data | Description | Remark
AA | Rectifier status | AA: 00-Rectifier off; 01-Rectifier on
BB | Inverter status | BB: 00-Inverter off; 01-Inverter on
CC | phase-locked states | CC:00-Locke off; 01-Unlock
DDDDD | Bypass status | DDDDD: "00000"means bypass OK else bypass abnormal
EEEEE | Grid status | EEEEE:"00000"means Grid OK else Grid abnormal
FF | EPO status | FF:00-EPO off; 01-EPO on
GG | Maintenance bypass status | GG:00-Maintenance bypass off; 01-Maintenance bypass on
HH | 开机命令标志 | HH:00-收到开机命令；01-未收到开机命令
^P008BATT?<CRC><cr>: Query battery test time
Response:^D006AAA<CRC><cr>
Data | Description | Remark
AAA | Test time | A: 0~9, unit: 1min
^P009DCHGT?<CRC><cr>:Query Discharge Time
Response:^D006AAA<CRC><cr>
Data | Description | Remark
AAA | Discharge Time | A: 0~9, unit: 1min
^P008FCID?<CRC><cr>:Query Factory ID
Response: ^DnnnAA,XXXXXXXXXXXXXXXXXXXXX<CRC><cr>
Data | Description | Remark
nnn | The available data length. | n:0~9, unit: 1
AA | The number of X, maximum is 21. | A:0~9, unit: 1
Example: ^D02014,01234567890123<CRC><cr>, it meas ID is 01234567890123.
^P009UPSTY?<CRC><cr>:Query UPS Type
Response: ^D005AA<CRC><cr>
Data | Description | Remark
AA | UPS Type | A: 0~9, unit: 1
^P008CTRP?<CRC><cr>:Query parameter Type
Response: ^D005AA<CRC><cr>
Data | Description | Remark
AAA | parameter Type | A: 0~9, unit: 1
^P008QVER2<CRC><cr>:Query CPU version
Response: ^D008aa,bb<CRC><cr>
Data | Description | Remark
aa | HD version | a: 0~9, unit: 1
bb | Power version | b: 0~9, unit: 1
^P006QRI<CRC><cr>：Query Rated Parameter
Response:^D032aaaaaa,bbb.b,cc.c,ddd.d,eee.e<CRC><cr>
Data | Description | Remark
aaaaaa | rated power | a: 0~9, unit: 1W
bbb.b | rated output voltege | b: 0~9, unit: 1V
cc.c | rated output frequency | c: 0~9, unit: 1Hz
ddd.d | rated output current | d: 0~9, unit: 1A
eee.e | rated battery voltage | e: 0~9, unit: 1V
^P006PAR<CRC><cr>：Query Single or parallel machine
Response:^D005aa<CRC><cr>
aa | Single or parallel | aa: 31 or 33
Set commands
^S006SON<CRC><cr>: Set enable machine supply power to the loads
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
ACK | Accept command
NAK | Refuse command
^S007SOFF<CRC><cr>: Set disable machine supply power to the loads
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
ACK | Accept command
NAK | Refuse command
^S009PEPDmn<CRC><cr>: Set enable/disable flag status
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
m | enable/disable | E: enable, D: disable
n | A | ECO mode
| B | CVCF mode
| C | Autorestart with battery
| D | Autorestart without battery
| E | Bypass
| F | auto to bypass
| Z | Reserve
ACK | Accept command
NAK | Refuse command
^S011SGVLHmmm<CRC><cr>: Set grid voltage high loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mmm | grid voltage high loss point | mmm: 235~285, unit: 1V
ACK | Accept command
NAK | Refuse command
^S011SGVLLmmm<CRC><cr>: Set grid voltage low loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mmm | grid voltage low loss point | mmm: 165~225, unit: 1V
ACK | Accept command
NAK | Refuse command
^S012SGFLHmm.m<CRC><cr>: Set grid frequency high loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mm.m | grid frequency high loss point | mmm: L~70.0, unit: 1Hz L: Low loss point
ACK | Accept command
NAK | Refuse command
^S012SGFLLmm.m<CRC><cr>: Set grid frequency low loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mm.m | grid frequency low loss point | mmm: 40.0~H, unit: 1Hz H: high loss point
ACK | Accept command
NAK | Refuse command
^S011SBVLHmmm<CRC><cr>: Set bypass voltage high loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mmm | bypass voltage high loss point | mmm: 235~285, unit: 1V
ACK | Accept command
NAK | Refuse command
^S011SBVLLmmm<CRC><cr>: Set bypass voltage low loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mmm | bypass voltage low loss point | mmm: 165~225, unit: 1V
ACK | Accept command
NAK | Refuse command
^S012SBFLHmm.m<CRC><cr>: Set bypass frequency high loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mm.m | bypass frequency high loss point | mmm: 51.0~56.0(@50Hz); 61.0~66.0(@60Hz) unit: 1Hz
ACK | Accept command
NAK | Refuse command
^S012SBFLLmm.m<CRC><cr>: Set bypass frequency low loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mm.m | bypass frequency low loss point | mmm: 45.0~49.0(@50Hz); 55.0~59.0(@60Hz) unit: 1Hz
ACK | Accept command
NAK | Refuse command
^S011SEVLHmmm<CRC><cr>: Set ECO voltage high loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mmm | ECO voltage high loss point | mmm: 235~285, unit: 1V
ACK | Accept command
NAK | Refuse command
^S011SEVLLmmm<CRC><cr>: Set ECO voltage low loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mmm | ECO voltage low loss point | mmm: 165~225, unit: 1V
ACK | Accept command
NAK | Refuse command
^S012SEFLHmm.m<CRC><cr>: Set ECO frequency high loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mm.m | ECO frequency high loss point | mmm: 51.0~56.0(@50Hz); 61.0~66.0(@60Hz) unit: 1Hz
ACK | Accept command
NAK | Refuse command
^S012SEFLLmm.m<CRC><cr>: Set ECO frequency low loss point
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mm.m | ECO frequency low loss point | mmm: 45.0~49.0(@50Hz); 55.0~59.0(@60Hz) unit: 1Hz
ACK | Accept command
NAK | Refuse command
^S009BATNnn<CRC><cr>: Set battery number
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
nn | battery number | nn: 28~32 unit: 1PCS
ACK | Accept command
NAK | Refuse command
^S009CHGInn<CRC><cr>: Set charging current
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
nn | charging current | nn: 00~15 unit: 1A
ACK | Accept command
NAK | Refuse command
^S012BULKVnn.n<CRC><cr>: Set charging bulk voltage
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
nn.n | bulk voltage | nn.n: F~14.0 unit: 1V F: Floating voltage
ACK | Accept command
NAK | Refuse command
^S012FLATVnn.n<CRC><cr>: Set charging floating voltage
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
nn.n | floating voltage | nn.n: 12.0~B unit: 1V B: Bulk voltage
ACK | Accept command
NAK | Refuse command
^S010CTFTnnn<CRC><cr>: Set the conversion time that constant voltage charging to floating
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
nnn | conversion time | nnn: 000~900 unit: 1min
ACK | Accept command
NAK | Refuse command
^S009OPVnnn<CRC><cr>: Set AC output voltage
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
nnn | output voltage | nnn: 220 or 230 or 240 unit: 1v
ACK | Accept command
NAK | Refuse command
^S008OPFnn<CRC><cr>: Set AC output frequency
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
nn | output frequency | nn:00 or 50 or 60 unit: 1Hz 00 means auto detect
ACK | Accept command
NAK | Refuse command
^S010BCAPnnn<CRC><cr>: Set battery capacity
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
nnn | battery capacity | nnn:050~600 unit: 1Ah
ACK | Accept command
NAK | Refuse command
^S009BGRPnn<CRC><cr>: Set battery group
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
nn | battery group | nn:01~06 unit: 1group
ACK | Accept command
NAK | Refuse command
^S0xxUSIDaabbbbbbbbbbbbbbbbbbbb<CRC><cr>: Set user ID
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
xx | The available data length.
aa | The number of X, maximum is 21. | a:0~9, unit: 1
b…b | This the ID number you want to set | maximum is 20.
ACK | Accept command
NAK | Refuse command
Example: ^S016USID071234567<CRC><cr>; it meas the ID is 1234567 you want to set.
^S010BATTmmm<CRC><cr>: Set battery test time
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mmm | Test time | mmm: 000~900, unit: 1min
ACK | Accept command
NAK | Refuse command
^S011BATTESTm<CRC><cr>: Set the battery test to start or end
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
m | Flag | m:0-end; 1-start
ACK | Accept command
NAK | Refuse command
^S011DCHGTmmm<CRC><cr>:Set battery Discharge Time
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mmm | Discharge Time | mmm: 000~900, unit: 1min
ACK | Accept command
NAK | Refuse command
^S0xxFCIDaabbbbbbbbbbbbbbbbbbbb<CRC><cr>: Set Factory ID
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
xx | The available data length.
aa | The number of X, maximum is 21. | a:0~9, unit: 1
b…b | This the ID number you want to set | maximum is 20.
ACK | Accept command
NAK | Refuse command
Example: ^S016FCID071234567<CRC><cr>; it meas the ID is 1234567 you want to set.
^S010UPSTYmm<CRC><cr>: Set UPS Type
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mm | Discharge Time | mm: 01~04, unit: 1
ACK | Accept command
NAK | Refuse command
^S009CTRPmm<CRC><cr>: Set parameter Type
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
mm | parameter Type | mm: 00~01, unit: 1
ACK | Accept command
NAK | Refuse command
^S011FCTRESTm<CRC><cr>: Set Factory reset
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
m | Factory reset Flag | m: B, F,U,O, unit: 1
ACK | Accept command
NAK | Refuse command
^S007CLFT<CRC><cr>: Set Clear Fault
Response: ^D006ACK<CRC><cr> or ^D006NAK<CRC><cr>
Data | Description | Remark
ACK | Accept command
NAK | Refuse command
^S009CFAULT<CRC><cr>: Set Eeprom Clear Fault
Response: ^D006ACK<CRC><cr>
Data | Description | Remark
ACK | Accept command

## Modified record
Modified record
Number | Author | Date | Modified content
1 | 王冰霜 | 2018-03-08 | 初版完成
2 | 王冰霜 | 2018-03-19 | 1.修改QPIWS的顺序，并增加充电板待机警告 2.增加fault说明 3.修正ID码设置命令的举例
3 | 李阳 | 2018-12-24 | 1.^P007QGS1 命令中增加S，T两相旁路电压 2.^P008PEPD? 命令修正了返回数据的长度 3.^P008QPIWS 命令充电去掉了充电线连接错误警告 4.^P010QFAULTn 新增了报错条例 5.修正^S008OPFnn，^S009BGRPnn设置命令 6.红色标记的命令为新增的设置和查询命令