## General Information
Delta UPS Modbus Version 02.10
General Information
SlaveID |  |  | 1 (Default)
Timeout |  |  | Least 200ms
Comment
Modbus RTU
Baud Rate |  |  | 19200
Parity |  |  | None
Data Bits |  |  | 8
Stop Bits |  |  | 1
Modbus TCP |  |  | IPv4
Server Port |  |  | 502 (Default)
Addresses Mode |  |  | Protocol Addresses Mode (Base 0)
Version history:
Date | Version | Author | Description
2017-11-11 | V00.00 | Richard Lin | 1. First draft
2017-11-23 | V00.01 | Gary Chu | 1. Add DPS project 2. Add 0x0A00 ~ 0x0AFF in Input sheet 3. Add DPS STS internal status(flag) sheet 4. Add DPS PFC internal status(flag) sheet 5. Add DPS INV internal status(flag) sheet 6. Add DPS CHG internal status(flag) sheet
2018-08-09 | V00.02 | Gary Chu | 1. Add HUASU BMS input and holding address.
2018-11-20 | V00.03 | Gary Chu | 1. Add 0x5101~0x5108 holding registry address.
2019-08-12 | V00.04 | Gary Chu | 1. Modify 0x405~0x406 Unit context.
2019-08-16 | V00.05 | Gary Chu | 1. Add Discrete Input/Coils/Holding sheet 2. Modify Input address. 3. Add support column for different machine type. 4. Delete DPS STS/PFC/INV/CHG internal statsus sheets
2019-12-31 | V00.06 | Gary Chu | 1. Add Input dry contact 800~803 [Holding]
2020-04-01 | V00.07 | Gary Chu | 1. Add Output dry contact 791~796 [Holding]
2020-04-08 | V02.08 | Gary Chu | 1. Add STS/PFC/INV internal stat(flag) sheet 2. Add Input/Output dry contact state 350~367 [Discrete Inputs]
2020-09-30 | V02.09 | Gary Chu | 1. Add 0x530 for Accumulated Run Time [Inputs] 2. Add 0x440 for Input Frequency [Input] 3. Delete unnecessary information in internal status. [STS/PFC/INV interfal status(flag)]
2021-05-31 | V02.10 | Gary Chu | 1. Merage DPH table in this file

## Coils
Coil (Read Function 01, Write Function 05 )
Address(DEC) | Address(HEX) | Description | Comment | Uint | DPH(3P4W) | DPH(3P3W) | DPS(3P4W) | DPH(3P4W) | DPH(3P3W) | DPS(3P3W)
UPS ( 0x200 ~ 0x206)
512 | 0x0200 | UPS Buzzer | 0 = Silence, 1 = Alarm |  | V | V | V | V | V | V
513 | 0x0201 | Reserved
514 | 0x0202 | Economic Mode Setting | 0 = Disable, 1 = Enable |  | V | V | V | V | V | V
515 | 0x0203 | Reserved
516 | 0x0204 | AC Fail & Restore Auto-Reboot | 0= Disable, 1 = Enable |  | V | V | V | V | V | V
517 | 0x0205 | Reserved
518 | 0x0206 | Enable/Disable Buzzer | 0 = Disable, 1 = Enable |  | V | V | V | V | V | V

## Discrete Inputs
Discrete Inputs (Read Function 02)
Address(DEC) | Address(HEX) | Description | Comment | Uint | DPH(3P4W) | DPH(3P3W) | DPS(3P4W) | DPH(3P4W) | DPH(3P3W) | DPS(3P3W)
UPS ( 0x100 ~ 0x12C)
256 | 0x0100 | Alarm Over Temperature | 0 = OK ; 1 = Over Temperature |  | V | V | V | V | V | V
257 | 0x0101 | Alarm Input Out Of Range | 0 = OK ; 1 = Input Bad |  | V | V | V | V | V | V
258 | 0x0102 | Alarm Output Bad | 0 = OK ; 1 = Output Bad
259 | 0x0103 | Alarm Overload | 0 = OK ; 1 = Overload |  | V | V | V | V | V | V
260 | 0x0104 | Alarm Bypass Out Of Range | 0 = OK ; 1 = Bypass Bad |  | V | V | V | V | V | V
261 | 0x0105 | Alarm Output Off | 0 = Output On ; 1 = Output Off |  | V | V | V | V | V | V
262 | 0x0106 | Alarm UPS Shutdown | 0 = OK ; 1 = Shutdown
263 | 0x0107 | Alarm Charger Fail | 0 = OK ; 1 = Charger Failed |  | V | V | V | V | V | V
264 | 0x0108 | Alarm Standby | 0 = Others ; 1 = Standby |  | V | V | V | V | V | V
265 | 0x0109 | Alarm Fan Fail | 0 = OK ; 1 = Fan Fault |  | V | V | V | V | V | V
266 | 0x010A | Alarm Fuse Fail | 0 = OK ; 1 = Fuse Fault |  | V | V | V | V | V | V
267 | 0x010B | Alarm Other Warning | 0 = OK ; 1 = General Fault |  | V | V | V | V | V | V
268 | 0x010C | Alarm Awaiting Power | 0 = OK ; 1 = Awaiting Power
269 | 0x010D | Alarm Shutdown Pending | 0 = OK ; 1 = Shutdown Pending
270 | 0x010E | Alarm Shutdown Imminent | 0 = OK ; 1 = Shutdown Imminent |  | V | V | V | V | V | V
271 | 0x010F | Buzzer Status | 0 = UPS Buzzer Silence 1 = UPS Buzzer is Alarming |  | V | V | V | V | V | V
272 | 0x0110 | Economic Mode | 0 = No ; 1 = Yes |  | V | V | V | V | V | V
273 | 0x0111 | Alarm Inverter Fail | 0 = No ; 1 = Yes
274 | 0x0112 | Emergency Power Off | 0 = Off ; 1 = On |  | V | V | V | V | V | V
275 | 0x0113 | Buzzer State | 0 = UPS Buzzer Disable 1 = UPS Buzzer Enable |  | V | V | V | V | V | V
276 | 0x0114 | Battery Ground Fault | 0: normal ; 1: ground fault |  | V | V | V | V | V | V
277 | 0x0115 | Alarm Redundancy Loss | 0: Normal, 1: Alarm |  | V | V | V | V | V | V
278 | 0x0116 | Alarm Output Breaker Open | 0: Close, 1: Open |  | V | V | V | V | V | V
279 | 0x0117 | Reserved
280 | 0x0118 | Reserved
281 | 0x0119 | Bypass Breaker Open | 0: Close, 1: Open |  | V | V | V | V | V | V
282 | 0x011A | Main Input Breaker Open | 0: Close, 1: Open |  | V | V | V | V | V | V
283 | 0x011B | Manual Bypass Breaker Open | 0: Close, 1: Open |  | V | V | V | V | V | V
284 ~ 295 | 0x011C ~ 0x0127 | Reserved
296 | 0x0128 | Alarm bypass voltage/ Frequency bad | 0 = OK 1 = Bypass Voltage/Frequency. Bad |  | V | V | V | V | V | V
297 | 0x0129 | Alarm bypass phase sequence bad | 0 = OK ; 1 = Bypass Phase Sequence Bad |  | V | V | V | V | V | V
298 | 0x012A | Alarm bypass STS overload | 0 = OK ; 1 = Bypass STS Overload |  |  |  | V |  |  | V
299 | 0x012B | Alarm bypass STS over temperature | 0 = OK ; 1 = Bypass STS Over Temperature |  | V | V | V | V | V | V
300 | 0x012C | Alarm bypass STS Fault | 0 = OK ; 1= Bypass STS Fault |  | V | V | V | V | V | V
301~349 | 0x12D~0x015D | Reserved
350 | 0x015E | Dry1 ouput state | 0 = relay open ; 1 = relay closed |  | V | V | V | V | V | V
351 | 0x015F | Dry2 ouput state | 0 = relay open ; 1 = relay closed |  | V | V | V | V | V | V
352 | 0x0160 | Dry3 ouput state | 0 = relay open ; 1 = relay closed |  | V | V | V | V | V | V
353 | 0x0161 | Dry4 ouput state | 0 = relay open ; 1 = relay closed |  | V | V | V | V | V | V
354 | 0x0162 | Dry5 ouput state | 0 = relay open ; 1 = relay closed |  | V | V | V | V | V | V
355 | 0x0163 | Dry6 ouput state | 0 = relay open ; 1 = relay closed |  | V | V | V | V | V | V
356 | 0x0164 | Option - Dry1 ouput state(Reserved) | 0 = relay open ; 1 = relay closed | [6 empty] | V
357 | 0x0165 | Option - Dry2 ouput state(Reserved) | 0 = relay open ; 1 = relay closed | [6 empty] | V
358 | 0x0166 | Option - Dry3 ouput state(Reserved) | 0 = relay open ; 1 = relay closed | [6 empty] | V
359 | 0x0167 | Option - Dry4 ouput state(Reserved) | 0 = relay open ; 1 = relay closed | [6 empty] | V
360 | 0x0168 | Option - Dry5 ouput state(Reserved) | 0 = relay open ; 1 = relay closed | [6 empty] | V
361 | 0x0169 | Option - Dry6 ouput state(Reserved) | 0 = relay open ; 1 = relay closed | [6 empty] | V
362 | 0x016A | Dry1 input state | 0 = relay open ; 1 = relay closed |  | V | V | V | V | V | V
363 | 0x016B | Dry2 input state | 0 = relay open ; 1 = relay closed |  | V | V | V | V | V | V
364 | 0x016C | Dry3 input state | 0 = relay open ; 1 = relay closed |  | V | V | V | V | V | V
365 | 0x016D | Dry4 input state | 0 = relay open ; 1 = relay closed |  | V | V | V | V | V | V
366 | 0x016E | Option - Dry1 input state(Reserved) | 0 = relay open ; 1 = relay closed | [6 empty] | V
367 | 0x016F | Option - Dry2 input state(Reserved) | 0 = relay open ; 1 = relay closed | [6 empty] | V

## Holding
Holding Registers (Read Function 03, Write Function 06) |  |  |  |  | Return = 0xFFFF(-1), NO Support |  | Return = 0xFFFF(-1), NO Support
Address(DEC) | Address(HEX) | Description | Comment | Uint | DPH(3P4W) | DPH(3P3W) | DPS(3P4W) | DPH(3P4W) | DPH(3P3W) | DPS(3P3W)
UPS ( 0x300 ~ 0x321)
768 | 0x0300 | UPS Shutdown Delay | 0~9999 (0=Abort) | Seconds
769 | 0x0301 | UPS Restart Delay | 0~65535,(65535 = Cancel restart) | Minutes
770 | 0x0302 | Test | 0 = Abort test 1 = General test (Obsolete) 2 = BTV test 3 = Test for 10 seconds 4 = Test until battery low
771 | 0x0303 | Reserved
772 | 0x0304 | Low Transfer Voltage | 0~999 | Volt | V | V | V | V | V | V
773 | 0x0305 | High Transfer Voltage | 0~999 | Volt | V | V | V | V | V | V
774 | 0x0306 | Voltage Sensitivity | 0 = Normal 1 = Reduced 2 = Low
775 | 0x0307 | Last Battery Replace Date - Year | 0~9999 | Year | V | V | V | V | V | V
776 | 0x0308 | Last Battery Replace Date - Month | 1~12 | Month | V | V | V | V | V | V
777 | 0x0309 | Last Battery Replace Date - Day | 1~31 | Day | V | V | V | V | V | V
778 | 0x030A | Next Battery Replace Date - Year | 0~9999 | Year | V | V | V | V | V | V
779 | 0x030B | Next Battery Replace Date - Month | 1~12 | Month | V | V | V | V | V | V
780 | 0x030C | Next Battery Replace Date - Day | 1~31 | Day | V | V | V | V | V | V
781 | 0x030D | UPS Periodic Auto-Test | 1 = Disable 2 = Daily 3 = Weekly 4 = BiWeekly 5 = Monthly
782 | 0x030E | Reserved
783 | 0x030F | UPS Boot Delay | 0~999 (Coils 0x0204 AC Fail & Restore Auto-Reboot = Enable) | Seconds
784 | 0x0310 | Bypass Frequency Tolerance | 0~50 | 0.1Hz | V | V | V | V | V | V
785 | 0x0311 | Reserved
786 | 0x0312 | Test Time | 1~60 | Minutes | V | V | V | V | V | V
787 | 0x0313 | Test Voltage | 0~999 | Volt | V | V | V | V | V | V
788~789 | 0x0314~0x0315 | Reserved
790 | 0x0316 | External Battery Pack | 0~10
791 | 0x0317 | Dry Contact W1 | High Byte B7: 0=Normal Open, 1=Normal Close B5 … B0: 0=None, 1=Dry Contact1, 2=Dry Contact2, …, 6=Dry Contact6 Low Byte B7: 0=Inactive, 1=Active B6 … B0: 0=None, 1=Event1, ... 20=Event20 Evt No. Event descriptor 0 = None, 1 = Load On Inverter, 2 = Load On Bypass, 3 = Load On Battery, 4 = Battery Low, 5 = Bypass Input Abnormal, 6 = Battery Test Fail, 7 = Internal Comm. Fail, 8 = External Parallel Comm. Fail, 9 = Output Overload, 10 = EPO Activated, 11 = Load On Manual Bypass, 12 = Battery Over Temperature, 13 = Output Voltage Abnormal, 14 = Battery Need Replacement, 15 = Bypass Over Temperature, 16 = Bypass Static Switch Fault, 17 = UPS Over Temperature, 18 = Battery Breaker Shunt Trip, 19 = Backfeed Protection, 20 = General Alarm |  | V | V | V | V | V | V
792 | 0x0318 | Dry Contact W2 |  |  | V | V | V | V | V | V
793 | 0x0319 | Dry Contact W3 |  |  | V | V | V | V | V | V
794 | 0x031A | Dry Contact W4 |  |  | V | V | V | V | V | V
795 | 0x031B | Dry Contact W5 |  |  | V | V | V | V | V | V
796 | 0x031C | Dry Contact W6 |  |  | V | V | V | V | V | V
797 | 0x031D | Bypass Low Transfer Voltage | 0~999 (Read Only) | Volt | V | V | V | V | V | V
798 | 0x031E | Bypass High Transfer Voltage | 0~999 (Read Only) | Volt | V | V | V | V | V | V
799 | 0x031F | Bypass Voltage Tolerance | 0~999 | Volt
800 | 0x0320 | Dry Contact Input Status 1 | High Byte Bit7: 0=Normal Open, 1=Normal Close Bit5 … Bit0: 0=None, 1=Dry Contact_in_1, 2=Dry Contact_in_2… Low Byte Bit7: 0=Inactive, 1=Active Bit6 … Bit0: 0=None, 1=Event1, ... 20=Event20 Evt No. Event descriptor 0 None 1 None (UPS ON/OFF) (no support in DPH) 2 None (Remote On/Off) (no support in DPH) 3 Generator Status 4 Battery Ground Fail 5 Ext Batt Breaker Detection 6 Battery Fuse Open 7 Charge Off (Positive) 8 Charge Off (Negative) 9 Power Off (Active Standby) 10 Battery Damage Shutdown 11 Input Transformer OTW 12 Output Transformer OTW 13 Charge Off (Total) |  | V | V | V | V | V | V
801 | 0x0321 | Dry Contact Input Status 2 |  |  | V | V | V | V | V | V
802 | 0x0322 | Dry Contact Input Status 2 |  |  | V | V | V | V | V | V
803 | 0x0323 | Dry Contact Input Status 2 |  |  | V | V | V | V | V | V

## Input
Input Registers (Read Function 04) |  |  |  |  | Return = 0xFFFF(-1), NO Support |  | Return = 0xFFFF(-1), NO Support
Address(DEC) | Address(HEX) | Description | Comment | Uint | DPH(3P4W) | DPH(3P3W) | DPS(3P4W) | DPH(3P4W) | DPH(3P3W) | DPS(3P3W)
UPS ( 0x400 ~ 0x4B0)
1024 | 0x0400 | Series | 0 to 5 0 = T, 1 = H, 2 = NT, 3 = NH, 4 = DPS, 5 = DPH |  | V | V | V | V | V | V
1025 | 0x0401 | Rating Input Voltage | 0 to 999 | Volt
1026 | 0x0402 | Rating Input Frequency | 0 to 999 | 0.1Hz
1027 | 0x0403 | Rating Output Voltage | 0 to 999 | Volt | V | V | V | V | V | V
1028 | 0x0404 | Rating Output Frequency | 0 to 999 | 0.1Hz | V | V | V | V | V | V
1029 | 0x0405 | Rating VA | 0 to 65534 | Unit 10VA -> DPS 600KVA Unit 1KVA | V | V | V | V | V | V
1030 | 0x0406 | Rating Output Power | 0 to 65534 | Unit 10Watt -> DPS 600KVA Unit 1KWatt | V | V | V | V | V | V
1031 | 0x0407 | Reserved
1032 | 0x0408 | Mains Input Low Tx Voltage Point | 0 to 999 | Volt | V | V | V | V | V | V
1033 | 0x0409 | Mains Input High Tx Voltage Point | 0 to 999 | Volt | V | V | V | V | V | V
1034 | 0x040A | Mains Input Low Tx Voltage Upper Bound | 0 to 999 | Volt | V | V | V | V | V | V
1035 | 0x040B | Mains Input Low Tx Voltage Lower Bound | 0 to 999 | Volt | V | V | V | V | V | V
1036 | 0x040C | Mains Input High Tx Voltage Upper Bound | 0 to 999 | Volt | V | V | V | V | V | V
1037 | 0x040D | Mains Input High Tx Voltage Lower Bound | 0 to 999 | Volt | V | V | V | V | V | V
1038 | 0x040E | UPS Type | 0 to 6 0: On-Line 1: Off-Line 2: Line-Interactive 3: 3 Phase 4: Split Phase 5: Others6: HVDC |  | V | V | V | V | V | V
1039 | 0x040F | Rating Battery Voltage | 0 to 999 | Volt | V | V | V | V | V | V
1040 | 0x0410 | Mains Low Tx Frequency Point |  | 0.1Hz | V | V | V | V | V | V
1041 | 0x0411 | Mains High Tx Frequency Point |  | 0.1Hz | V | V | V | V | V | V
1042 | 0x0412 | Bypass Rating Freq | 0 to 999 | 0.1Hz | V | V | V | V | V | V
1043 | 0x0413 | Bypass Freq Max Tolerance | 5 to 50 | 0.1Hz | V | V | V | V | V | V
1044 | 0x0414 | Bypass Freq Set Tolerance | 5 to 50 | 0.1Hz | V | V | V | V | V | V
1045 | 0x0415 | Bypass Low Tx Voltage Point/ Bypass Rating Voltage | 0 to 999 | Volt | V | V | V | V | V | V
1046 | 0x0416 | Bypass High Tx Voltage Point | 0 to 999 | Volt | V | V | V | V | V | V
1047 | 0x0417 | Bypass Low Tx Voltage Upper Bound/ Bypass Voltage Max Tolerance (obsolete) | 0 to 999 | Volt
1048 | 0x0418 | Bypass Low Tx Voltage Lower Bound/ Bypass Voltage Set Tolerance (obsolete) | 0 to 999 | Volt
1049 | 0x0419 | Bypass High Tx Voltage Upper Bound (obsolete) | 0 to 999 | Volt
1050 | 0x041A | Bypass High Tx Voltage Lower Bound (obsolete) | 0 to 999 | Volt
1051~1053 | 0x041B~0x041D | Reserved
1054 | 0x041E | Battery Condition | 0 = Good 1 = Weak 2 = Replace |  | V | V | V | V | V | V
1055 | 0x041F | Battery Status | 0 to 2 0 = OK, 1 = Low, 2 = Depleted |  | V | V | V | V | V | V
1056 | 0x0420 | Battery Charge | 0 to 3 0 = (obsolete), 1 = Charging, 2 = Resting, 3 = Discharging |  | V | V | V | V | V | V
1057 | 0x0421 | Seconds on Battery | 0 to 99999 | Seconds | V | V | V | V | V | V
1058 | 0x0422 | Estimated Minutes Remaining | 0 to 9999 | Estimated time from backup to low battery shutdown. | V | V | V | V | V | V
1059 | 0x0423 | Estimated Charge Remaining (not used, reserved) | 0 to 999 | Estimated of percent battery charge remaining. | V | V | V | V | V | V
1060 | 0x0424 | Battery Voltage | 0 to 9999 | 0.1Volt | V | V | V | V | V | V
1061 | 0x0425 | Battery Current | 0 to 9999 | 0.1Amp | V | V | V | V | V | V
1062 | 0x0426 | UPS Internal Temperature | 0 to 999 | Degree Celsius | V | V | V | V | V | V
1063 | 0x0427 | Battery Level | 0 to 100 | % | V | V | V | V | V | V
1064 | 0x0428 | External Batt-Pack Number | 0 to 10 | Number of External Battery Pack | V | V | V | V | V | V
1065 | 0x0429 | Negative Battery Voltage | 0 to 9999 | -0.1Volt | V |  | V | V
1066 | 0x042A | Negative Battery Current | 0 to 9999 | 0.1Amp | V |  | V | V
1067 | 0x042B | Reserved
1068 | 0x042C | Negative Battery Level | 0 to 999 | % | V |  | V | V
1069 | 0x042D | Positive Charging Current | 0 to 9999 | 0.1Amp | V |  | V | V
1070 | 0x042E | Negative Charging Current | 0 to 9999 | 0.1Amp | V |  | V | V
1071 | 0x042F | Battery Charge Mode | 0 to 3 0 = None, 1 = Boost charge, 2 = Float charge, 3 = Discharge |  | V | V | V | V | V | V
1072 | 0x0430 | Input Num Lines(Phases) | 0 to 9 |  | V | V | V | V | V | V
1073 | 0x0431 | Input Frequency1 | 0 to 999 | 0.1Hz | V |  | V | V
1074 | 0x0432 | Input Voltage1 | 0 to 9999 | 0.1Volt | V |  | V | V
1075 | 0x0433 | Input Current1 | 0 to 9999 | Amp | V | V | V | V | V | V
1076 | 0x0434 | Input Power1 | 0 to 65534 | 10 Watt
1077 | 0x0435 | Input Frequency2 | 0 to 999 | 0.1Hz | V |  | V | V
1078 | 0x0436 | Input Voltage2 | 0 to 9999 | 0.1Volt | V |  | V | V
1079 | 0x0437 | Input Current2 | 0 to 9999 | Amp | V | V | V | V | V | V
1080 | 0x0438 | Input Power2 | 0 to 65534 | 10 Watt
1081 | 0x0439 | Input Frequency3 | 0 to 999 | 0.1Hz | V |  | V | V
1082 | 0x043A | Input Voltage3 | 0 to 9999 | 0.1Volt | V |  | V | V
1083 | 0x043B | Input Current3 | 0 to 9999 | Amp | V | V | V | V | V | V
1084 | 0x043C | Input Power3 | 0 to 65534 | 10 Watt
1085 | 0x043D | Input Voltage12 | 0 to 9999 | 0.1Volt | V | V | V | V | V | V
1086 | 0x043E | Input Voltage23 | 0 to 9999 | 0.1Volt | V | V | V | V | V | V
1087 | 0x043F | Input Voltage31 | 0 to 9999 | 0.1Volt | V | V | V | V | V | V
1088 | 0x0440 | Input Frequency | 0 to 999 | 0.1Hz |  |  | V | V | V
1089 | 0x0441 | Total Output Power Factor | 0 to 999 | KW/KVA % | V | V | V | V | V | V
1090 | 0x0442 | Output Source | 0 to 7 0 = Normal 1 = Battery 2 = Bypass (3phase Reserve Power Path) 3 = Reducing 4 = Boosting 5 = Manual Bypass 6 = Other 7 = No output 8 = On ECO |  | V | V | V | V | V | V
1091 | 0x0443 | Output Frequency | 0 to 999 | 0.1Hz | V | V | V | V | V | V
1092 | 0x0444 | Output Num Lines(Phase) | 0 to 9 | Number of output lines | V | V | V | V | V | V
1093 | 0x0445 | Output Voltage1 | 0 to 9999 | 0.1Volt | V |  | V | V
1094 | 0x0446 | Output Current1 | 0 to 65534 | 0.1Amp | V | V | V | V | V | V
1095 | 0x0447 | Output Power1 | 0 to 65534 | 10 Watt | V |  | V | V
1096 | 0x0448 | Output Load1 | 0 to 999 | Percent | V |  | V | V
1097 | 0x0449 | Output Voltage2 | 0 to 9999 | 0.1Volt | V |  | V | V
1098 | 0x044A | Output Current2 | 0 to 65534 | 0.1Amp | V | V | V | V | V | V
1099 | 0x044B | Output Power2 | 0 to 65534 | 10 Watt | V |  | V | V
1100 | 0x044C | Output Load2 | 0 to 999 | Percent | V |  | V | V
1101 | 0x044D | Output Voltage3 | 0 to 9999 | 0.1Volt | V |  | V | V
1102 | 0x044E | Output Current3 | 0 to 65534 | 0.1Amp | V | V | V | V | V | V
1103 | 0x044F | Output Power3 | 0 to 65534 | 10 Watt | V |  | V | V
1104 | 0x0450 | Output Load3 | 0 to 999 | Percent | V |  | V | V
1105 | 0x0451 | Output Voltage12 | 0 to 9999 | 0.1Volt | V | V | V | V | V | V
1106 | 0x0452 | Output Voltage23 | 0 to 9999 | 0.1Volt | V | V | V | V | V | V
1107 | 0x0453 | Output Voltage31 | 0 to 9999 | 0.1Volt | V | V | V | V | V | V
1108 | 0x0454 | Total Output Power KW | 0 to 65534 | 0.1KW | V | V | V | V | V | V
1109 | 0x0455 | Total Output Power KVA | 0 to 65534 | 0.1KVA | V | V | V | V | V | V
1110 | 0x0456 | Bypass Frequency | 0 to 999 | 0.1Hz | V | V | V | V | V | V
1111 | 0x0457 | Bypass Num Lines(Phase) | 0 to 9 | Number of bypass lines | V | V | V | V | V | V
1112 | 0x0458 | Bypass Voltage1 | 0 to 9999 | 0.1Volt | V |  | V | V
1113 | 0x0459 | Bypass Current1 | 0 to 99999 | 0.1Amp
1114 | 0x045A | Bypass Power1 | 0 to 999999 | 10Watt
1115 | 0x045B | Bypass Voltage2 | 0 to 9999 | 0.1Volt | V |  | V | V
1116 | 0x045C | Bypass Current2 | 0 to 99999 | 0.1Amp
1117 | 0x045D | Bypass Power2 | 0 to 999999 | 10Watt
1118 | 0x045E | Bypass Voltage3 | 0 to 9999 | 0.1Volt | V |  | V | V
1119 | 0x045F | Bypass Current3 | 0 to 99999 | 0.1Amp
1120 | 0x0460 | Bypass Power3 | 0 to 999999 | 10Watt
1121 | 0x0461 | Bypass Voltage12 | 0 to 9999 | 0.1Volt | V | V | V | V | V | V
1122 | 0x0462 | Bypass Voltage23 | 0 to 9999 | 0.1Volt | V | V | V | V | V | V
1123 | 0x0463 | Bypass Voltage31 | 0 to 9999 | 0.1Volt | V | V | V | V | V | V
1124 | 0x0464 | Bypass STS Temperature | 0 to 999 | Degree Celsius | V | V | V | V | V | V
1125 ~ 1126 | 0x0465 ~ 0x0466 | Reserved
1127 | 0x0467 | Test Result | 0 to 5 0 = No test performed 1 = Test passed 2 = Test in progress 3 = General test failed (Obsolete) 4 = Battery test failed 5 = Deep battery test failed (Obsolete) 6 = Test Aborted |  | V | V | V | V | V | V
1128 | 0x0468 | Number of Output Relay |  | 0 : Not Available > 0 : Available(<=99)
1129 | 0x0469 | Temperature |  | 0.1 Degree Celsius
1130 | 0x046A | Humidify |  | %
1131 | 0x046B | Relay 1 | 0 : Off, 1 : On, 0xFFFF: NO Connect
1132 | 0x046C | Relay 2 | 0 : Off, 1 : On, 0xFFFF: NO Connect
1133 | 0x046D | Relay 3 | 0 : Off, 1 : On, 0xFFFF: NO Connect
1134 | 0x046E | Relay 4 | 0 : Off, 1 : On, 0xFFFF: NO Connect
1135 | 0x046F | Reserved
1136 | 0x0470 | Output Power Factor 1 |  | KW/KVA % | V |  | V | V
1137 | 0x0471 | Output Power Factor 2 |  | KW/KVA % | V |  | V | V
1138 | 0x0472 | Output Power Factor 3 |  | KW/KVA % | V |  | V | V
1139 ~ 1154 | 0x0473~0x0482 | Reserved
1155 | 0x0483 | UPS Event Log Entry | 0 to 500
1156 | 0x0484 | Event log report format | 0: NT 9 byte format 1: NH 8 byte format 2: Online 6 byte format
1157 | 0x0485 | Event Reporting method | 0: ELS 1: EVT
1158 | 0x0486 | Battery Cabinet #1 Temperature | 0 – 999 | Degree Celsius | V | V | V | V | V | V
1159 | 0x0487 | Battery Cabinet #2 Temperature | 0 – 999 | Degree Celsius | V | V | V | V | V | V
1160 | 0x0488 | Battery Cabinet #3 Temperature | 0 – 999 | Degree Celsius | V | V | V | V | V | V
1161 | 0x0489 | Battery Cabinet #4 Temperature | 0 – 999 | Degree Celsius | V | V | V | V | V | V
1162 | 0x048A | Battery cabinet breaker | 1: close, 0:open |  | V | V | V | V | V | V
1163 ~ 1174 | 0x048B~0x0496 | Reserved
1175 | 0x0497 | Model Byte 0, 1 | Lo: Byte0, Hi: Byte 1 |  | V | V | V | V | V | V
1176 | 0x0498 | Model Byte 2, 3 | Lo: Byte2, Hi: Byte 3 |  | V | V | V | V | V | V
1177 | 0x0499 | Model Byte 4, 5 | Lo: Byte4, Hi: Byte 5 |  | V | V | V | V | V | V
1178 | 0x049A | Model Byte 6, 7 | Lo: Byte6, Hi: Byte 7 |  | V | V | V | V | V | V
1179 | 0x049B | Model Byte 8, 9 | Lo: Byte8, Hi: Byte 9 |  | V | V | V | V | V | V
1180 | 0x049C | Model Byte 10, 11 | Lo: Byte10, Hi: Byte 11 |  | V | V | V | V | V | V
1181 | 0x049D | Model Byte 12, 13 | Lo: Byte12, Hi: Byte 13 |  | V | V | V | V | V | V
1182 | 0x049E | Model Byte 14, 15 | Lo: Byte14, Hi: Byte 15 |  | V | V | V | V | V | V
1183 ~ 1185 | 0x049F~0x04A1 | Reserved
1186 | 0x04A2 | Firmware Version Byte 0, 1 | Lo: Byte0, Hi: Byte 1 |  | V | V | V | V | V | V
1187 | 0x04A3 | Firmware Version Byte 2, 3 | Lo: Byte2, Hi: Byte 3 |  | V | V | V | V | V | V
1188 | 0x04A4 | Firmware Version Byte 4, 5 | Lo: Byte4, Hi: Byte 5 |  | V | V | V | V | V | V
1189 | 0x04A5 | Firmware Version Byte 6, 7 | Lo: Byte6, Hi: Byte 7 |  | V | V | V | V | V | V
1190 | 0x04A6 | Firmware Version Byte 8, 9 | Lo: Byte8, Hi: Byte 9 |  | V | V | V | V | V | V
1191 | 0x04A7 | Firmware Version Byte 10, 11 | Lo: Byte10, Hi: Byte 11 |  | V | V | V | V | V | V
1192 | 0x04A8 | Firmware Version Byte 12, 13 | Lo: Byte12, Hi: Byte 13 |  | V | V | V | V | V | V
1193 | 0x04A9 | Firmware Version Byte 14, 15 | Lo: Byte14, Hi: Byte 15 |  | V | V | V | V | V | V
1194 ~ 1196 | 0x04AA~0x04AC | Reserved
1197 | 0x04AD | CPU Byte 0, 1 | Lo: Byte0, Hi: Byte 1
1198 | 0x04AE | CPU Byte 2, 3 | Lo: Byte2, Hi: Byte 3
1199 | 0x04AF | Reserved
1200 | 0x04B0 | UPS Connection Status | 0:Disconnection 1:Connection |  | V | V | V | V | V | V
1201 | 0x04B1 | Total Output Load |  | % | V |  | V | V
UPS Control System Unit(CSU) Status ( 0x500 ~ 0x504)
1280 | 0x0500 | CSU-Aux power#1 repair status | 0: Normal 1: Repair |  | V | V | V | V | V | V
1281 | 0x0501 | CSU-Aux power#2 repair status |  |  | V | V | V | V | V | V
1282 | 0x0502 | CSU-STS repair status |  |  | V | V | V | V | V | V
1283 | 0x0503 | CSU-Comm#1 repair status |  |  | V | V | V | V | V | V
1284 | 0x0504 | CSU-Comm#2 repair status |  |  | V | V | V | V | V | V
Get the UPS Internal Tim ( 0x530 ~ 0x550)
1328 | 0x0530 | Accumulated Run Time | 0 to 65534 | day | V | V |  |  | V
UPS information ( 0x600 ~ 0xFFF)
1536 | 0x0600 | STS module repair status | 0: Normal 1: Repair |  |  |  |  | V | V
1537 | 0x0601 | STS module-Temp-1 |  |  | V | V | V | V | V | V
1538 | 0x0602 | STS module-Temp-2 |  |  | V | V | V | V | V | V
1539 | 0x0603 | STS module-Temp-3 |  |  | V | V | V | V | V | V
1540 | 0x0604 | STS module-Temp-4 (Reserved) |  |  | V | V | V | V | V | V
1541 | 0x0605 | STS module-Temp-5 (Reserved) |  |  | V | V | V | V | V | V
1542 | 0x0606 | STS module-Temp-6 (Reserved) |  |  | V | V | V | V | V | V
1552 | 0x0610 | STS module-Fan Speed-1 |  |  | V | V | V | V | V | V
1553 | 0x0611 | STS module-Fan Speed-2 |  |  | V | V | V | V | V | V
1554 | 0x0612 | STS module-Fan Speed-3 |  |  | V | V | V | V | V | V
1555 | 0x0613 | STS module-Fan Speed-4 (Reserved) |  |  | V | V | V | V | V | V
1556 | 0x0614 | STS module-Fan Speed-5 (Reserved) |  |  | V | V | V | V | V | V
1557 | 0x0615 | STS module-Fan Speed-6 (Reserved) |  |  | V | V | V | V | V | V
1776 | 0x06F0 | General Alarm | 0 : normal 1: alarm in STS internal status/flag #0~17 |  |  |  | V | V | V
1792~1809 | 0x0700 ~ 0x0711 | STS internal status/flag #0~17 | STS internal status(flag) Refer to UPS MonCAN protocol doc |  | V | V | V | V | V | V
2048~2063 | 0x0800 ~ 0x080F | PFC 1 internal status/flag #0 ~ 15 | PFC internal status(flag) Refer to UPS MonCAN protocol doc |  | V | V | V | V | V | V
2064~2079 | 0x0810 ~ 0x081F | PFC 2 internal status/flag #0 ~ 15 |  |  | V | V | V | V | V | V
~ | ~ | ~ |  |  | V | V | V | V | V | V
2288~2303 | 0x08F0 ~ 0x08FF | PFC 16 internal status/flag #0 ~ 15 |  |  | V | V | V | V | V | V
2304~2319 | 0x0900 ~ 0x090F | INV 1 internal status/flag #0 ~ 15 | INV internal status(flag) Refer to UPS MonCAN protocol doc |  | V | V | V | V | V | V
2320~2335 | 0x0910 ~ 0x091F | INV 2 internal status/flag #0 ~ 15 |  |  | V | V | V | V | V | V
~ | ~ | ~ |  |  | V | V | V | V | V | V
2544~2559 | 0x09F0 ~ 0x09FF | INV 16 internal status/flag #0 ~ 15 |  |  | V | V | V | V | V | V
2560~2575 | 0x0A00~0x0A0F | CHG 1 internal status/flag #0 ~ 15 | CHG internal status(flag) Refer to UPS MonCAN protocol doc |  |  |  | V |  |  | V
2576~2591 | 0x0A10~0x0A1F | CHG 2 internal status/flag #0 ~ 15 |  |  |  |  | V |  |  | V
~ | ~ | ~ |  |  |  |  | V |  |  | V
2800~2815 | 0x0AF0~0x0AFF | CHG 16 internal status/flag #0 ~ 15 |  |  |  |  | V |  |  | V
2900~2915 | 0x0B54~0x0B63 | AM internal status/flag #0~15 | AM internal status(flag) Refer to AM internal stats(flag) sheet |  |  | V |  |  | V
Power Module Information ( 0x1000 ~ )
PM ID(1~16) |  | 1 | Excel 手動輸入左側數據，可產出各PM的address
PM Address (Decimal) |  | 4096 + (64 * (PM ID -1))+Index
4096 | 0x1000 | Attribute | Bit0: PFC Bit1: Rectifier Bit2: Charger Bit3: Inverter Bit4: Bypass Bit5: TBD Bit6: TBD Bit7: TBD |  | V | V | V | V | V | V
4097 | 0x1001 | General Status | Bit0: The power module exist or the power module is powered Bit1: OFF Bit2: Repair (NH+: The front screw is open) Bit3: Fault shutdown |  | V | V | V | V | V | V
4098 | 0x1002 | PFC Status | Bit0: PFC fuse open fault Bit1: PFC over temperature warning Comment Bit2: PFC over temperature shutdown Bit3: DC bus over voltage warning Bit4: DC bus over voltage shutdown Bit5: DC bus under voltage warning Bit6: DC bus under voltage shutdown Bit7: PFC circuit general fault Bit8: Fan failure Bit9: Output Current Limit Bit10: PFC Off Bit11: Inner communication failure Bit12: Not calibrated (used to indicate whether the power module has been calibrated) Bit13: Battery fuse open warning |  | V | V | V | V | V | V
4099 | 0x1003 | Inverter Status | Bit0: Inverter fuse open Bit1: Inverter over temperature warning Bit2: Inverter over temperature shutdown Bit3: Fan failure Bit4: Inverter short circuit Bit5: Inverter STS failure Bit6: Inverter voltage abnormal Bit7: Inverter circuit general fault shutdown Bit8: DC bus over voltage shutdown Bit9: Inverter overload Bit10: Inner communication loss (includes the comm. to system or other modules) Bit11: EPO shutdown Bit12: Inverter parallel communication loss Bit13: Inverter parallel failure (which may due to any of ID, or rating setting conflict, etc…) Bit14: STS on/off. 1:on,0:off. Bit15: Not calibrated (used to indicate whether the power module has been calibrated) |  | V | V | V | V | V | V
4100 | 0x1004 | Charger Status | Bit0: Charger circuit general fault Bit1-Bit7: Reserved |  | V | V | V | V | V | V
4101 | 0x1005 | Temperature - PFC | Temperature: 0 - 9999 | Degree Celsius | V | V | V | V | V | V
4102 | 0x1006 | Temperature - TBD |  | Degree Celsius
4103 | 0x1007 | Temperature – Inverter |  | Degree Celsius | V | V | V | V | V | V
4104 | 0x1008 | Temperature – Inverter R |  | Degree Celsius | V | V | V | V | V | V
4105 | 0x1009 | Temperature – Inverter S |  | Degree Celsius | V | V | V | V | V | V
4106 | 0x100A | Temperature – Inverter T |  | Degree Celsius | V | V | V | V | V | V
4107 | 0x100B | Inverter Voltage R | Voltage: 0 - 9999 | 0.1Volt | V |  | V | V
4108 | 0x100C | Inverter Voltage S |  | 0.1Volt | V |  | V | V
4109 | 0x100D | Inverter Voltage T |  | 0.1Volt | V |  | V | V
4110 | 0x100E | +Bus Voltage |  | 0.1Volt | V | V | V | V | V | V
4111 | 0x100F | -Bus Voltage |  | 0.1Volt | V | V | V | V | V | V
4112 | 0x1010 | OUTPUT VOLTAGE-RS |  | 0.1Volt
4113 | 0x1011 | OUTPUT VOLTAGE-ST |  | 0.1Volt
4114 | 0x1012 | OUTPUT VOLTAGE-TR |  | 0.1Volt
4115 | 0x1013 | OUTPUT CURRENT-R |  | 0.1Amp | V | V | V | V | V | V
4116 | 0x1014 | OUTPUT CURRENT-S |  | 0.1Amp | V | V | V | V | V | V
4117 | 0x1015 | OUTPUT CURRENT-T |  | 0.1Amp | V | V | V | V | V | V
4118 | 0x1016 | OUTPUT FREQUENCY |  | 0.1Hz | V | V | V | V | V | V
4119 | 0x1017 | Temperature – PFC R | Temperature: 0 - 9999 | Degree Celsius | V | V | V | V | V | V
4120 | 0x1018 | Temperature – PFC S |  | Degree Celsius | V | V | V | V | V | V
4121 | 0x1019 | Temperature – PFC T |  | Degree Celsius | V | V | V | V | V | V
4122 | 0x101A | CHARGER VOLTAGE+ | Voltage: 0 - 9999 | 0.1Volt | V | V | V | V | V | V
4123 | 0x101B | CHARGER VOLTAGE- |  | 0.1Volt | V | V | V | V | V | V
4124 | 0x101C | CHARGER CURRENT+ |  | 0.1Amp | V | V | V | V | V | V
4125 | 0x101D | CHARGER CURRENT- |  | 0.1Amp | V | V | V | V | V | V
4126 | 0x101E | A/D Status | 0: Off 1: ON |  | V | V | V | V | V | V
4127 | 0x101F | D/D Status | 0: Off 1: ON |  | V | V | V | V | V | V

## DPS STS internal status(flag)
STS internal status/flag #0 - Severity 0 (for SubN)
| DPS Definition | Remark
b0 | Energy Storage State Off
b1 | Charge Off (Postive)
b2 | Charge Off (Negative)
b3 | Charge Off
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #1 - Severity 0 (for Sub2)
| Definition | Remark
b0 | Diesel Gen In
b1 | TBD
b2 | TBD
b3 | TBD
b4 | TBD
b5 | Inv PLL Ref Async to Bypass
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #2 - Severity 0 (for Sub1)
| Definition | Remark
b0 | Bat Test Passed
b1 | Bat Test Abort
b2 | Bat Test In Progress
b3 | Bat Baseline Test Passed
b4 | Bat Baseline Test Abort
b5 | Bat Baseline Test In Progress
b6 | On Bypass
b7 | On Bat
b8 | Online
b9 | No Output
b10 | On ECO
b11 | On energy recycle
b12 | Const Bat Current Discharge
b13 | Starting
b14 | Global MCU Upgrade Mode
b15 | Global FPGA Upgrade Mode
STS internal status/flag #3 - Severity 0 (for Sub1)
| Definition | Remark
b0 | STS MCU Upgrade
b1 | STS FPGA Upgrade
b2 | On Frequency Convert Mode
b3 | Manual Set Equalize Charge
b4 | Manual Abort Equalize Charge
b5 | UPS Off Cmd
b6 | UPS On Cmd
b7 | Battery Charge
b8 | Battery Rest
b9 | Battery Discharge
b10 | On Energy Storage State
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #4 - Severity 1 (for SubN)
| Definition | Remark
b0 | Main Volt Abnormal
b1 | Bypass Volt Out ECO Range
b2 | Li-Ion Batt Communication Abnormal
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #5 - Severity 1 (for Sub2)
| Definition | Remark
b0 | Bypass Volt Abnormal
b1
b2
b3 | Bypass Volt Seq Abnormal
b4 | Main Volt Seq Abnormal
b5 | Main freq abnormal
b6 | Main Switch Off
b7 | Bypass Switch Off
b8 | Output Switch Off
b9 | Manual Bypass Breaker On
b10 | Active Standby
b11 | Replace Dust Filter
b12 | Online To ECO Inhibit
b13 | Bypass Freq Abnormal
b14 | External Bypass Switch Off
b15 | External Main Switch Off
STS internal status/flag #6 - Severity 1 (for Sub2)
| Definition | Remark
b0 | External Output Switch Off
b1 | External Battery Breaker Off
b2 | Li-Ion Batt Over Volt Warning
b3 | Li-Ion Batt Under Volt Warning
b4 | Li-Ion Batt Over Temperature Warning
b5 | Li-Ion Batt Under Temperature Warning
b6 | Li-Ion Batt Over Current Warning
b7 | Li-Ion Batt Unbalance Warning
b8 | Li-Ion Batt Over Discharge Warning
b9 | TBD
b10 | Li-Ion Batt Hardware Abnormal
b11 | Output Common Mode Volt Too High
b12 | Li-ion Battery Neutral Wire Config Incompatible
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #7 - Severity 1 (for Sub1)
| Definition | Remark
b0 | Bat Life Expired
b1 | TBD
b2 | TBD
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #8 - Severity 2 (for SubN)
| Definition | Remark
b0 | TBD
b1 | TBD
b2 | TBD
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #9 - Severity 2 (for Sub2)
| Definition | Remark
b0 | Output Overload Warning
b1 | PM Redundant Loss
b2 | Over Overload Auto Recover Limit
b3 | Over Inv Volt Abnormal Auto Recover Limit
b4 | Bat Low Warning
b5 | Bat Disconnected
b6 | Bat Reversed
b7 | Bat Gnd Fault
b8 | Bat Over Temp
b9 | Bypass STS OT Warning R
b10 | Bypass STS OT Warning S
b11 | Bypass STS OT Warning T
b12 | Bypass STS module NTC Not Installed
b13 | Ambient NTC Not Installed
b14 | Bat Under temp
b15 | STS Fan Power Board Over Temp
STS internal status/flag #10 - Severity 2 (for Sub2)
| Definition | Remark
b0 | Input Transformer Over Temperature Warning
b1 | Output Transformer Over Temperature Warning
b2 | UnderEnergyStorageBatProtVolt
b3 | Battery Damage Warning
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #11 - Severity 2 (for Sub1)
| Definition | Remark
b0 | Bat Test Fail
b1 | Bat Baseline Test Fail
b2 | TBD
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #12 - Severity 3 (for SubN)
| Definition | Remark
b0 | Output Overload Critical
b1 | TBD
b2 | EPOActive
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #13 - Severity 3 (for Sub2)
| Definition | Remark
b0 | Parallel Setting Conflict
b1 | Parallel Setting Incompatible - AC In type
b2 | Parallel Setting Incompatible - Bat type
b3 | Parallel Setting Incompatible - Output type
b4
b5
b6 | EXTCAN Com Abnormal
b7 | Aux power on repair #1
b8 | Aux power on repair #2
b9 | Aux power fail #1
b10 | Aux power fail #2
b11 | INTCAN Bus1Abnormal
b12 | INTCAN Bus2 Abnormal
b13 | EXTCAN Bus1 Abnormal
b14 | EXTCAN Bus2 Abnormal
b15 | MONCAN Bus1 Abnormal
STS internal status/flag #14 - Severity 3 (for Sub2)
| Definition | Remark
b0 | MONCAN Bus2Abnormal
b1 | PioAbnormal
b2 | Inv PLL Ref Bus Abnormal
b3
b4
b5
b6
b7
b8 | PMAbsent_1
b9 | PMAbsent_2
b10 | PMAbsent_3
b11 | PMAbsent_4
b12 | PMAbsent_5
b13 | PMAbsent_6
b14 | PMAbsent_7
b15 | PMAbsent_8
STS internal status/flag #15 - Severity 3 (for Sub2)
| Definition | Remark
b0 | PMAbsent_9
b1 | PMAbsent_10
b2 | PMAbsent_11
b3 | PMAbsent_12
b4 | PMAbsent_13
b5 | PMAbsent_14
b6 | PMAbsent_15
b7 | PMAbsent_16
b8 | COM1Absent
b9 | COM2Absent
b10 | TouchPanelAbsent
b11 | STSFPGAConfigFail
b12 | BatOverCharge
b13
b14 | System Fan Aux Pwr Fail
b15 | External frame abnormal loss
STS internal status/flag #16 - Severity 3 (for Sub2)
| Definition | Remark
b0 | STS Module Fan1 Abnormal
b1 | STS Module Fan2 Abnormal
b2 | STS Module Fan3 Abnormal
b3 | STS Module Fan4 Abnormal
b4 | STS Module Fan5 Abnormal
b5 | STS Module Fan6 Abnormal
b6 | STS Module Fan7 Abnormal
b7 | STS Module Fan8 Abnormal
b8 | STS Module Fan9 Abnormal
b9 | STS Module Fan10 Abnormal
b10 | STS Module Fan11 Abnormal
b11 | STS Module Fan12 Abnormal
b12 | STS Module Fan13 Abnormal
b13 | STS Module Fan14 Abnormal
b14 | STS Module Fan15 Abnormal
b15 | STS Module Fan16 Abnormal
STS internal status/flag #17 - Severity 3 (for Sub1)
| Definition | Remark
b0 | Bypass STS Open
b1 | Bypass STS Short
b2 | Output Short Circuit
b3 | Battery Damage Shutdown
b4 | Battery Fuse Open
b5
b6 | Main BackFeed
b7 | EOD
b8 | InvVolt Abnormal R
b9 | InvVolt Abnormal S
b10 | InvVolt Abnormal T
b11 | Bypass STS OTP R
b12 | Bypass STS OTP S
b13 | Bypass STS OTP T
b14 | TBD
b15 | TBD
STS internal status/flag #18 - Severity 3 (for Sub2)
| Definition | Remark
b0 | STS Module Fan17 Abnormal
b1 | STS Module Fan18 Abnormal
b2 | STS Module Fan19 Abnormal
b3 | STS Module Fan20 Abnormal
b4 | STS Module Fan21 Abnormal
b5 | STS Module Fan22 Abnormal
b6 | STS Module Fan23 Abnormal
b7 | STS Module Fan24 Abnormal
b8
b9
b10
b11
b12
b13
b14
b15
STS internal status/flag #19 - Severity 3 (for Sub1)
| Definition | Remark
b0 | Output Transformer Over Heat Shutdown
b1 | Input Transformer Over Heat Protection
b2 | Bypass STS Short R
b3 | Bypass STS Short S
b4 | Bypass STS Short T
b5 | Bypass STS Fuse 1 Open
b6 | Bypass STS Fuse 2 Open
b7 | Bypass STS Fuse 3 Open
b8 | Bypass STS Fuse 4 Open
b9 | Bypass STS Fuse 5 Open
b10 | Bypass STS Fuse 6 Open
b11 | Bypass STS Fuse 7 Open
b12 | Bypass STS Fuse 8 Open
b13 | Bypass STS Fuse 9 Open
b14
b15

## DPS PFC internal status(flag)
PFC internal status/flag #0 (PFC state machine) |  | PFC internal status/flag #1 (over recover limit event)
b0 | stand by mode | b0 | PFC DC Bus over voltage over recover limit
b1 | soft start mode | b1 | PFC DC Bus under voltage over recover limit
b2 | PFC AC mode | b2 | PFC over temperature over recover limit
b3 | PFC DC mode | b3
b4 | PFC const current mode | b4
b5 | PFC discharge | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
PFC internal status/flag #2 (AC input volt) |  | PFC internal status/flag #3 (output)
b0 | AC input volt phase R RMS out ot of range | b0 | PFC PBus over voltage warning
b1 | AC input volt phase S RMS out ot of range | b1 | PFC NBus over voltage warning
b2 | AC input volt phase T RMS out ot of range | b2 | PFC PBus under voltage warning
b3 |  | b3 | PFC NBus under voltage warning
b4 |  | b4 | PFC PBus discharged
b5 |  | b5 | PFC Nbus discharged
b6 |  | b6
b7 |  | b7
b8 | AC input volt frequency out of range | b8 | PFC PBus over instanteous voltage critical
b9 | AC input volt sequence abnormal | b9 | PFC NBus over instanteous voltage critical
b10 |  | b10 | PFC PBus over voltage critical
b11 |  | b11 | PFC NBus over voltage critical
b12 | Self-Diagnosis Abnormal - Main Input Voltage R | b12 | PFC PBus under voltage critical
b13 | Self-Diagnosis Abnormal - Main Input Voltage S | b13 | PFC NBus under voltage critical
b14 | Self-Diagnosis Abnormal - Main Input Voltage T | b14 | PFC Bus over volt hardware detection
b15 |  | b15
PFC internal status/flag #4 (AC input curr) |  | PFC internal status/flag #5 (power cell1 temperature)
b0 | AC input current unbalance warning RS | b0 | PFC power cell 1 over heat warning R
b1 | AC input current unbalance warning ST | b1 | PFC power cell 1 over heat warning S
b2 | AC input current unbalance warning TR | b2 | PFC power cell 1 over heat warning T
b3 |  | b3
b4 | AC input current unbalance critical RS | b4
b5 | AC input current unbalance critical ST | b5
b6 | AC input current unbalance critical TR | b6
b7 |  | b7
b8 | AC input power cell current unbalance warning R | b8 | PFC power cell 1 over heat critical R
b9 | AC input power cell current unbalance warning S | b9 | PFC power cell 1 over heat critical S
b10 | AC input power cell current unbalance warning T | b10 | PFC power cell 1 over heat critical T
b11 |  | b11
b12 | AC input power cell current unbalance critical R | b12
b13 | AC input power cell current unbalance critical S | b13
b14 | AC input power cell current unbalance critical T | b14
b15 |  | b15
PFC internal status/flag #6 (power cell2 temperature) |  | PFC internal status/flag #7 (power cell3 temperature)
b0 | PFC power cell 2 over heat warning R | b0 | PFC power cell 3 over heat warning R
b1 | PFC power cell 2 over heat warning S | b1 | PFC power cell 3 over heat warning S
b2 | PFC power cell 2 over heat warning T | b2 | PFC power cell 3 over heat warning T
b3 |  | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 | PFC power cell 2 over heat critical R | b8 | PFC power cell 3 over heat critical R
b9 | PFC power cell 2 over heat critical S | b9 | PFC power cell 3 over heat critical S
b10 | PFC power cell 2 over heat critical T | b10 | PFC power cell 3 over heat critical T
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
PFC internal status/flag #8 (SCR cell temperature) |  | PFC internal status/flag #9 (fan auxpower temperture)
b0 | SCR cell over heat warning R | b0 | fan auxpower over heat warning
b1 | SCR cell over heat warning S | b1
b2 | SCR cell over heat warning T | b2
b3 |  | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 | SCR cell over heat critical R | b8
b9 | SCR cell over heat critical S | b9
b10 | SCR cell over heat critical T | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
PFC internal status/flag #10 (communication) |  | PFC internal status/flag #11 (component)
b0 | PFC-INV local communication loss | b0 | PFC power cell 1 small isolation fuse open
b1 | PFC-Charger local communication loss | b1 | PFC power cell 2 small isolation fuse open
b2 | Monitor CAN communication loss | b2 | PFC power cell 3 small isolation fuse open
b3 |  | b3
b4 | CAN Bus Redundant Fault 1 | b4 | INV supervisor fault
b5 | CAN Bus Redundant Fault 2 | b5 | Fan auxpower fault
b6 |  | b6
b7 |  | b7
b8 |  | b8 | Main input fuse open
b9 |  | b9 | Battery fuse open positive
b10 |  | b10 | Battery fuse open negative
b11 |  | b11 | Battery fuse open
b12 |  | b12 | PFC power cell 1 big isolation fuse open
b13 |  | b13 | PFC power cell 2 big isolation fuse open
b14 |  | b14 | PFC power cell 3 big isolation fuse open
b15 |  | b15
PFC internal status/flag #12 (NTC) |  | PFC internal status/flag #13 (fan)
b0 | PFC power cell 1 thermal NTC open R | b0 | PFC power cell 1 fan fault 1
b1 | PFC power cell 1 thermal NTC open S | b1 | PFC power cell 1 fan fault 2
b2 | PFC power cell 1 thermal NTC open T | b2 | PFC power cell 1 fan fault 3
b3 | PFC power cell 2 thermal NTC open R | b3 | PFC power cell 1 fan fault 4
b4 | PFC power cell 2 thermal NTC open S | b4 | PFC power cell 2 fan fault 1
b5 | PFC power cell 2 thermal NTC open T | b5 | PFC power cell 2 fan fault 2
b6 | PFC power cell 3 thermal NTC open R | b6 | PFC power cell 2 fan fault 3
b7 | PFC power cell 3 thermal NTC open S | b7 | PFC power cell 2 fan fault 4
b8 | PFC power cell 3 thermal NTC open T | b8 | PFC power cell 3 fan fault 1
b9 | SCR cell thermal NTC open R | b9 | PFC power cell 3 fan fault 2
b10 | SCR cell thermal NTC open S | b10 | PFC power cell 3 fan fault 3
b11 | SCR cell thermal NTC open T | b11 | PFC power cell 3 fan fault 4
b12 | Fan auxpower thermal NTC open | b12 | SCR cell fan fault 1
b13 |  | b13 | SCR cell fan fault 2
b14 |  | b14 | SCR cell fan fault 3
b15 |  | b15 | IO entry fan fault
PFC internal status/flag #14 (operation) |  | PFC internal status/flag #15 (miscellaneous)
b0 | AC mode scr soft start fail | b0 | EEPROM parameter uncalibrated
b1 | AC mode pwm soft start fail | b1
b2 | DC mode relay soft start fail | b2
b3 | DC mode pwm soft start fail | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
PFC internal status/flag #16 (DC input volt) |  | PFC internal status/flag #17 (AC input volt2)
b0 | PosiBatteryReversed | b0 | AC input volt phase RS RMS out ot of range
b1 | NegBatteryReversed | b1 | AC input volt phase ST RMS out ot of range
b2 | PosiBatteryUnderVolt | b2 | AC input volt phase TR RMS out ot of range
b3 | NegBatteryUnderVolt | b3
b4 | BatteryReversed | b4
b5 | BatteryUnderVolt | b5
b6 |  | b6
b7 |  | b7
b8 | Self-Diagnosis Abnormal - Battery Voltage - Positive | b8
b9 | Self-Diagnosis Abnormal - Battery Voltage - Negative | b9
b10 | Self-Diagnosis Abnormal - Battery Voltage | b10
b11 |  | b11
b12 |  | b12 | Self-Diagnosis Abnormal - Main Input Voltage RS
b13 |  | b13 | Self-Diagnosis Abnormal - Main Input Voltage ST
b14 |  | b14 | Self-Diagnosis Abnormal - Main Input Voltage TR
b15 |  | b15

## DPS INV internal status(flag)
INV internal status/flag #0 |  | INV internal status/flag #1
b0 | Standby mode | b0 | PM Load unbalance Warning-R
b1 | Soft start mode | b1 | PM Load unbalance Warning-S
b2 | Inverter ready mode | b2 | PM Load unbalance Warning-T
b3 | Voltage mode | b3 | Cell Load unbalance Warning-R
b4 | EnergyRecycling mode | b4 | Cell Load unbalance Warning-S
b5 | ConstBattCurrDischarge mode | b5 | Cell Load unbalance Warning-T
b6 | Deenergized mode | b6 | Cell Load unbalance Critical-R
b7 |  | b7 | Cell Load unbalance Critical-S
b8 |  | b8 | Cell Load unbalance Critical-T
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #2 |  | INV internal status/flag #3
b0 | INV Cell1 R NTC NOT Installed | b0 | INV Cell1 DC CAP Over Heat Warning
b1 | INV Cell1 S NTC NOT Installed | b1 | INV Cell2 DC CAP Over Heat Warning
b2 | INV Cell1 T NTC NOT Installed | b2 | INV Cell3 DC CAP Over Heat Warning
b3 | INV Cell2 R NTC NOT Installed | b3 | INV Cell1 R phase AC CAP Fault Warning
b4 | INV Cell2 S NTC NOT Installed | b4 | INV Cell1 S phase AC CAP Fault Warning
b5 | INV Cell2 T NTC NOT Installed | b5 | INV Cell1 T phase AC CAP Fault Warning
b6 | INV Cell3 R NTC NOT Installed | b6 | INV Cell2 R phase AC CAP Fault Warning
b7 | INV Cell3 S NTC NOT Installed | b7 | INV Cell2 S phase AC CAP Fault Warning
b8 | INV Cell3 T NTC NOT Installed | b8 | INV Cell2 T phase AC CAP Fault Warning
b9 | INV Cell1 DC Cap NTC NOT Installed | b9 | INV Cell3 R phase AC CAP Fault Warning
b10 | INV Cell2 DC Cap NTC NOT Installed | b10 | INV Cell3 S phase AC CAP Fault Warning
b11 | INV Cell3 DC Cap NTC NOT Installed | b11 | INV Cell3 T phase AC CAP Fault Warning
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #4 |  | INV internal status/flag #5
b0 | DC bus P over volt warning | b0
b1 | DC bus N over volt warning | b1
b2 | DC bus P over volt critical - slow | b2
b3 | DC bus N over volt critical - slow | b3
b4 | DC bus P over volt critical - fast | b4
b5 | DC bus N over volt critical - fast | b5
b6 | DC bus P under volt warning | b6
b7 | DC bus N under volt warning | b7
b8 | DC bus P under volt critical | b8
b9 | DC bus N under volt critical | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #6 |  | INV internal status/flag #7
b0 | output relay open critical | b0 | over temperature Cell1 R warning
b1 | output relay short critical | b1 | over temperature Cell1 S warning
b2 | PFC Supervisor Fault | b2 | over temperature Cell1 T warning
b3 | fuse open | b3 | over temperature Cell2 R warning
b4 | EEPROM parameter uncalibrated | b4 | over temperature Cell2 S warning
b5 |  | b5 | over temperature Cell2 T warning
b6 |  | b6 | over temperature Cell3 R warning
b7 |  | b7 | over temperature Cell3 S warning
b8 |  | b8 | over temperature Cell3 T warning
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #8 |  | INV internal status/flag #9
b0 | PM local communication loss warning | b0
b1 |  | b1
b2 | Mon CAN communication loss | b2
b3 |  | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6 | over current critical-HW
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #10 |  | INV internal status/flag #11
b0 | output short circuit R critical | b0 | PWM carrier PLL Fail
b1 | output short circuit S critical | b1 | Monitor CAN #1 redundant fault
b2 | output short circuit T critical | b2 | Monitor CAN #2 redundant fault
b3 | output short circuit RS critical | b3 | Internal CAN #1 redundant fault
b4 | output short circuit ST critical | b4 | Internal CAN #2 redundant fault
b5 | output short circuit TR critical | b5 | Parallel IO fault
b6 |  | b6 | Line Freq Bus fault
b7 |  | b7 | PWM Carrier LOSS fault
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #12 |  | INV internal status/flag #13
b0 | Soft start R phase fail | b0
b1 | Soft start S phase fail | b1
b2 | Soft start T phase fail | b2
b3 | DC offset voltage R fault warning | b3
b4 | DC offset voltage S fault warning | b4
b5 | DC offset voltage T fault warning | b5
b6 | DC offset voltage R fault critical | b6
b7 | DC offset voltage S fault critical | b7
b8 | DC offset voltage T fault critical | b8
b9 | Self-Diagnosis Abnormal - Output Voltage R | b9
b10 | Self-Diagnosis Abnormal - Output Voltage S | b10
b11 | Self-Diagnosis Abnormal - Output Voltage T | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 | phase lock fail | b15
INV internal status/flag #14 |  | INV internal status/flag #15
b0 | Over OTP auto recover limit | b0 | over temperature Cell1 R critical
b1 | Over OVP auto recover limit | b1 | over temperature Cell1 S critical
b2 | Over UVP auto recover limit | b2 | over temperature Cell1 T critical
b3 | Over OCP auto recover limit | b3 | over temperature Cell2 R critical
b4 |  | b4 | over temperature Cell2 S critical
b5 |  | b5 | over temperature Cell2 T critical
b6 |  | b6 | over temperature Cell3 R critical
b7 |  | b7 | over temperature Cell3 S critical
b8 |  | b8 | over temperature Cell3 T critical
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #16 |  | INV internal status/flag #17
b0 | Soft start RS line fail | b0 | PM Load unbalance Warning
b1 | Soft start ST line fail | b1
b2 | Soft start TR line fail | b2
b3 | DC offset voltage RS fault warning | b3 | Cell Load unbalance Warning-R
b4 | DC offset voltage ST fault warning | b4 | Cell Load unbalance Warning-S
b5 | DC offset voltage TR fault warning | b5 | Cell Load unbalance Warning-T
b6 | DC offset voltage RS fault critical | b6 | Cell Load unbalance Critical-R
b7 | DC offset voltage ST fault critical | b7 | Cell Load unbalance Critical-S
b8 | DC offset voltage TR fault critical | b8 | Cell Load unbalance Critical-T
b9 | Self-Diagnosis Abnormal - Output Voltage RS | b9
b10 | Self-Diagnosis Abnormal - Output Voltage ST | b10
b11 | Self-Diagnosis Abnormal - Output Voltage TR | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 | phase lock fail | b15

## DPS CHG internal status(flag)
CHG internal status/flag #0 |  | CHG internal status/flag #1
b0 | Operation mode - Debug | b0 | CHG on
b1 | Operation mode - Single PM | b1
b2 | Operation mode - Normal | b2
b3 |  | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 | Standby mode | b8
b9 | Charger mode | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
CHG internal status/flag #2 |  | CHG internal status/flag #3
b0 | Parameter not calibrated | b0 | CHG over temp. warning_P1
b1 |  | b1 | CHG over temp. warning_N1
b2 |  | b2 | CHG over temp. warning_P2
b3 |  | b3 | CHG over temp. warning_N2
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 | DC bus over voltage warning_P | b8
b9 | DC bus over voltage warning_N | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
CHG internal status/flag #4 |  | CHG internal status/flag #5
b0 | CHG fan fault 1 | b0 | CHG thermal sensor not installed_P1
b1 | CHG fan fault 2 | b1 | CHG thermal sensor not installed_N1
b2 | CHG fan fault 3 | b2 | CHG thermal sensor not installed_P2
b3 |  | b3 | CHG thermal sensor not installed_N2
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
CHG internal status/flag #6 |  | CHG internal status/flag #7
b0 |  | b0
b1 |  | b1
b2 |  | b2
b3 |  | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
CHG internal status/flag #8 |  | CHG internal status/flag #9
b0 |  | b0 | Monitor CAN communication loss
b1 |  | b1 | Local bus communication loss
b2 |  | b2
b3 |  | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
CHG internal status/flag #10 |  | CHG internal status/flag #11
b0 |  | b0 | CHG over temp. shutdown_P1
b1 |  | b1 | CHG over temp. shutdown_N1
b2 |  | b2 | CHG over temp. shutdown_P2
b3 |  | b3 | CHG over temp. shutdown_N2
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 | DC bus over voltage shutdown_P | b8
b9 | DC bus over voltage shutdown_N | b9
b10 | DC bus over voltage shutdown_HwIO | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
CHG internal status/flag #12 |  | CHG internal status/flag #13
b0 |  | b0 | Over CHG OT shutdown recover limit
b1 |  | b1
b2 |  | b2
b3 |  | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 | CHG fuse open_P | b14
b15 | CHG fuse open_N | b15
CHG internal status/flag #14 |  | CHG internal status/flag #15
b0 | CHG soft start fail_P1 | b0 | CHG under voltage_P1
b1 | CHG soft start fail_N1 | b1 | CHG under voltage_N1
b2 | CHG soft start fail_P2 | b2 | CHG under voltage_P2
b3 | CHG soft start fail_N2 | b3 | CHG under voltage_N2
b4 |  | b4
b5 |  | b5
b6 | CHG soft start fail_1 | b6 | CHG under voltage_1
b7 | CHG soft start fail_2 | b7 | CHG under voltage_2
b8 | CHG over voltage_P1 | b8 | CHG over current_P1
b9 | CHG over voltage_N1 | b9 | CHG over current_N1
b10 | CHG over voltage_P2 | b10 | CHG over current_P2
b11 | CHG over voltage_N2 | b11 | CHG over current_N2
b12 |  | b12
b13 |  | b13
b14 | CHG over voltage_1 | b14 | CHG over current_1
b15 | CHG over voltage_2 | b15 | CHG over current_2

## DPH STS internal status(flag)
STS internal status/flag
STS internal status/flag #0 - Severity 0 (for SubN)
| Definition | Remark
b0 | Terminate Diesel Generator Test | Subcode: 0x01: Test Inhibited 0x02: Abnormally Terminated 0x03: Terminated by Instruction 0x04: Terminated by Timeout
b1 | TBD
b2 | TBD
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #1 - Severity 0 (for Sub2)
| Definition | Remark
b0 | Diesel Gen In
b1 | Enter burn in mode (UPS operation configuration type)
b2 | TBD
b3 | TBD
b4 | TBD
b5 | Inv PLL Ref Async to Bypass
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #2 - Severity 0 (for Sub1)
| Definition | Remark
b0 | Bat Test Passed
b1 | Bat Test Abort
b2 | Bat Test In Progress
b3 | Bat Baseline Test Passed
b4 | Bat Baseline Test Abort
b5 | Bat Baseline Test In Progress
b6 | On Bypass
b7 | On Bat
b8 | Online
b9 | No Output
b10 | On ECO
b11 | On energy recycle
b12 | Const Bat Current Discharge
b13 | Starting
b14 | Global MCU Upgrade Mode
b15 | Global FPGA Upgrade Mode
STS internal status/flag #3 - Severity 0 (for Sub1)
| Definition | Remark
b0 | STS MCU Upgrade
b1 | STS FPGA Upgrade
b2 | Start Diesel Generator Test
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #4 - Severity 1 (for SubN)
| Definition | Remark
b0 | Main Volt Abnormal
b1 | Bypass Volt Out ECO Range
b2 | TBD
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal statuss/flag #5 - Severity 1 (for Sub2)
| Definition | Remark
b0 | Bypass Volt Abnormal
b1
b2
b3 | Bypass Volt Seq Abnormal
b4 | Main Volt Seq Abnormal
b5 | Main freq abnormal
b6 | Main Breaker Off
b7 | Bypass Breaker Off
b8 | Out Breaker Off
b9 | Manual Bypass Breaker On
b10 | Non Volatile Memory Parameter Not Calibrated
b11 | Replace Dust Filter
b12 | Online To ECO Inhibit
b13 | Bypass Freq Abnormal
b14 | TBD
b15 | TBD
STS internal status/flag #6 - Severity 1 (for Sub2)
| Definition | Remark
b0 | TBD
b1 | TBD
b2 | TBD
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #7 - Severity 1 (for Sub1)
| Definition | Remark
b0 | Bat Life Expired
b1 | TBD
b2 | TBD
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #8 - Severity 2 (for SubN)
| Definition | Remark
b0 | TBD
b1 | TBD
b2 | TBD
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #9 - Severity 2 (for Sub2)
| Definition | Remark
b0 | Output Overload Warning
b1 | PM Redundant Loss
b2 | Over Overload Auto Recover Limit
b3 | Over Inv Volt Abnormal Auto Recover Limit
b4 | Bat Low Warning
b5 | Bat Disconnected
b6 | Bat Reversed
b7 | Bat Gnd Fault
b8 | Bat Over Temp
b9 | Bypass STS Over Temp R
b10 | Bypass STS Over Temp S
b11 | Bypass STS Over Temp T
b12 | Bypass STS module NTC Not Installed
b13 | Ambient NTC Not Installed
b14 | Bat Under temp
b15 | Bat breaker trip
STS internal status/flag #10 - Severity 2 (for Sub2)
| Definition | Remark
b0 | TBD
b1 | TBD
b2 | TBD
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #11 - Severity 2 (for Sub1)
| Definition | Remark
b0 | Bat Test Fail
b1 | Bat Baseline Test Fail
b2 | TBD
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #12 - Severity 3 (for SubN)
| Definition | Remark
b0 | Output Overload Critical
b1 | Output Short Circuit
b2 | EPOActive
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #13 - Severity 3 (for Sub2)
| Definition | Remark
b0 | Parallel Setting Conflict
b1 | System Fan Fail
b2 | rev
b3 | STS Module Fan1 Abnormal
b4 | STS Module Fan2 Abnormal
b5 | STS Module Fan3 Abnormal
b6 | EXTCAN Com Abnormal
b7 | Aux power on repair #1
b8 | Aux power on repair #2
b9 | Aux power fail #1
b10 | Aux power fail #2
b11 | INTCAN Bus1Abnormal
b12 | INTCAN Bus2 Abnormal
b13 | EXTCAN Bus1 Abnormal
b14 | EXTCAN Bus2 Abnormal
b15 | MONCAN Bus1 Abnormal
STS internal status/flag #14 - Severity 3 (for Sub2)
| Definition | Remark
b0 | MONCAN Bus2Abnormal
b1 | PioAbnormal
b2 | Inv PLL Ref Bus Abnormal:
b3 | x
b4 | STS IOExp I2C Abnormal | x
b5 | COM1 IOExp I2CAbnormal
b6 | COM2 IOExp I2CAbnormal
b7 | STS Card Removed
b8 | PMAbsent_1
b9 | PMAbsent_2
b10 | PMAbsent_3
b11 | PMAbsent_4
b12 | PMAbsent_5
b13 | PMAbsent_6
b14 | PMAbsent_7
b15 | PMAbsent_8
STS internal status/flag #15 - Severity 3 (for Sub2)
| Definition | Remark
b0 | PMAbsent_9
b1 | PMAbsent_10
b2 | PMAbsent_11
b3 | PMAbsent_12
b4 | PMAbsent_13
b5 | PMAbsent_14
b6 | PMAbsent_15
b7 | PMAbsent_16
b8 | COM1Absent
b9 | COM2Absent
b10 | TouchPanelAbsent
b11 | STSFPGAConfigFail
b12 | BatOverCharge
b13 | STSModuleOnRepair
b14 | STSModuleAuxPwrFail
b15 | External frame abnormal loss
STS internal status/flag #16 - Severity 3 (for Sub2)
| Definition | Remark
b0 | Parallel Setting Incompatible - AC In type
b1 | Parallel Setting Incompatible - Bat type
b2 | Parallel Setting Incompatible - Output type
b3 | TBD
b4 | TBD
b5 | TBD
b6 | TBD
b7 | TBD
b8 | TBD
b9 | TBD
b10 | TBD
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD
STS internal status/flag #17 - Severity 3 (for Sub1)
| Definition | Remark
b0 | Bypass STS Open
b1 | Bypass STS Short
b2
b3
b4
b5
b6 | Main BackFeed
b7 | EOD
b8 | InvVolt Abnormal R
b9 | InvVolt Abnormal S
b10 | InvVolt Abnormal T
b11 | TBD
b12 | TBD
b13 | TBD
b14 | TBD
b15 | TBD

## DPH PFC internal status(flag)
PFC internal status/flag
PFC internal status/flag #0 (PFC state machine) |  | PFC internal status/flag #1 (charger state machine)
b0 | stand by mode | b0 | Charger off
b1 | soft start mode | b1 | Charger softstart
b2 | PFC AC mode | b2 | Charger on
b3 | PFC DC mode | b3
b4 | PFC const current mode | b4
b5 | PFC discharge | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
PFC internal status/flag #2 (AC input source) |  | PFC internal status/flag #3 (output)
b0 | AC input volt phase R RMS out ot of range | b0 | PFC PBus over voltage warning
b1 | AC input volt phase S RMS out ot of range | b1 | PFC NBus over voltage warning
b2 | AC input volt phase T RMS out ot of range | b2 | PFC PBus under voltage warning
b3 |  | b3 | PFC NBus under voltage warning
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 | AC input volt frequency out of range | b8 | PFC PBus over instanteous voltage critical
b9 | AC input volt sequence abnormal | b9 | PFC NBus over instanteous voltage critical
b10 |  | b10 | PFC PBus over voltage critical
b11 |  | b11 | PFC NBus over voltage critical
b12 |  | b12 | PFC PBus under voltage critical
b13 |  | b13 | PFC NBus under voltage critical
b14 |  | b14 | PFC Bus over volt hardware detection
b15 |  | b15
PFC internal status/flag #4 (charger) |  | PFC internal status/flag #5 (temperature)
b0 | Charger P voltage abnormal | b0 | Rectifier phase R over temperature warning
b1 | Charger N voltage abnormal | b1 | Rectifier phase S over temperature warning
b2 |  | b2 | Rectifier phase T over temperature warning
b3 |  | b3 | Charger over temperature warning
b4 | Charger P current abnormal | b4
b5 | Charger N current abnormal | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8 | Rectifier phase R over temperature critical
b9 |  | b9 | Rectifier phase S over temperature critical
b10 |  | b10 | Rectifier phase T over temperature critical
b11 |  | b11 | Charger over temperature critical
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
PFC internal status/flag #6 (communication) |  | PFC internal status/flag #7 (component)
b0 | PM local communication loss | b0 | Fan lock detection
b1 |  | b1 | Repair switch open
b2 | Monitor CAN communication loss | b2
b3 |  | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8 | Main input fuse open
b9 |  | b9 | Battery fuse open
b10 |  | b10 | Charger fuse open_P
b11 |  | b11 | Charger fuse open_N
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
PFC internal status/flag #8 (operation) |  | PFC internal status/flag #9 (miscellaneous)
b0 | soft start fail | b0 | EEPROM parameter uncalibrated
b1 |  | b1
b2 |  | b2
b3 |  | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15

## DPH INV internal status(flag)
INV internal status/flag
INV internal status/flag #0 |  | INV internal status/flag #1
b0 | Standby mode | b0
b1 | Soft start mode | b1
b2 | Inverter ready mode | b2
b3 | Voltage mode | b3
b4 | EnergyRecycling mode | b4
b5 | Const battery current discharge mode | b5
b6 | Deenergized mode | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #2 |  | INV internal status/flag #3
b0 |  | b0
b1 |  | b1
b2 |  | b2
b3 |  | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #4 |  | INV internal status/flag #5
b0 | DC bus P over volt warning | b0 | inverter phase voltage R critical
b1 | DC bus N over volt warning | b1 | inverter phase voltage S critical
b2 | DC bus P over volt critical - slow | b2 | inverter phase voltage T critical
b3 | DC bus N over volt critical - slow | b3
b4 | DC bus P over volt critical - fast | b4
b5 | DC bus N over volt critical - fast | b5
b6 | DC bus P under volt warning | b6
b7 | DC bus N under volt warning | b7
b8 | DC bus P under volt critical | b8
b9 | DC bus N under volt critical | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #6 |  | INV internal status/flag #7
b0 | output relay R phase open | b0 | over temperature R warning
b1 | output relay S phase open | b1 | over temperature S warning
b2 | output relay T phase open | b2 | over temperature T warning
b3 | output relay R phase short | b3 | over temperature R critical
b4 | output relay S phase short | b4 | over temperature S critical
b5 | output relay T phase short | b5 | over temperature T critical
b6 | fuse open | b6
b7 | current sensing R abnormal | b7
b8 | current sensing S abnormal | b8
b9 | current sensing T abnormal | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #8 |  | INV internal status/flag #9
b0 | PM local communication loss warning | b0 | over current R warning
b1 | INT CAN communication loss warning | b1 | over current S warning
b2 | monitor CAN communication loss warning | b2 | over current T warning
b3 |  | b3 | over current R critical
b4 |  | b4 | over current S critical
b5 |  | b5 | over current T critical
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #10 |  | INV internal status/flag #11
b0 | output short circuit R critical | b0 | PWM carrier fault
b1 | output short circuit S critical | b1 | Monitor CAN redundant fault
b2 | output short circuit T critical | b2 | Monitor CAN redundant fault2
b3 | output short circuit RS critical | b3 | Internal CAN redundant fault
b4 | output short circuit ST critical | b4 | Internal CAN redundant fault2
b5 | output short circuit TR critical | b5 | Parallel IO fault
b6 |  | b6 | Line Freq fault
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #12 |  | INV internal status/flag #13
b0 | Soft start R phase fail | b0 | EEPROM parameter uncalibrated
b1 | Soft start S phase fail | b1
b2 | Soft start T phase fail | b2
b3 | DC offset voltage R fault warning | b3
b4 | DC offset voltage S fault warning | b4
b5 | DC offset voltage T fault warning | b5
b6 | DC offset voltage R fault critical | b6
b7 | DC offset voltage S fault critical | b7
b8 | DC offset voltage T fault critical | b8
b9 | current sharing R phase unbalance | b9
b10 | current sharing S phase unbalance | b10
b11 | current sharing T phase unbalance | b11
b12 | phase lock fail | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
INV internal status/flag #14 |  | INV internal status/flag #15
b0 | Over OTP auto recover limit | b0 | Output VoltDiff Abnormal R
b1 | Over OVP auto recover limit | b1 | Output VoltDiff Abnormal S
b2 | Over UVP auto recover limit | b2 | Output VoltDiff Abnormal T
b3 | Over OCP auto recover limit | b3
b4 | Over VDP auto recover limit | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15

## DPH AM internal status(flag)
AM Diagnosis State Flag #0 |  | AM Diagnosis State Flag #1
Bit | Description | Bit | Description
b0 | IO Module on Repair | b0 | Batt. Fuse Open
b1 |  | b1 | Main Fuse Open
b2 | MONCAN Redundant Fault 1 | b2 | Bypass Fuse Open
b3 | MONCAN Redundant Fault 2 | b3
b4 |  | b4 | Main SPD Dry Contact Active
b5 |  | b5 | Bypass SPD Dry Contact Active
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15
AM Diagnosis State Flag #2 |  | AM Diagnosis State Flag #3
Bit | Description | Bit | Description
b0 | Exhaust Fan Aux Power Fault | b0 | AM Fan Aux Power Over Temperature Warning
b1 |  | b1 | AM Ambient Over Temperature Warning
b2 | AM MC Aux Power_01 Fail | b2 | AM Fan Aux Power Over Temperature Critical
b3 | AM MC Aux Power_02 Fail | b3
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 | AM MC R Phase Fault - Open | b10
b11 | AM MC S Phase Fault - Open | b11
b12 | AM MC T Phase Fault - Open | b12
b13 | AM MC R Phase Fault - Short | b13
b14 | AM MC S Phase Fault - Short | b14
b15 | AM MC T Phase Fault - Short | b15
AM Diagnosis State Flag #4
Bit | Description
b0 | Bypass Input Backfeed Fault
b1 | Bypass Input Phase R Backfeed Fault
b2 | Bypass Input Phase S Backfeed Fault
b3 | Bypass Input Phase S Backfeed Fault
b4
b5
b6
b7
b8
b9
b10
b11
b12
b13
b14
b15
AM Diagnosis State Flag #5 |  | AM Diagnosis State Flag #6
Bit | Description | Bit | Description
b0 | Exhaust Fan #1 Fault | b0 | Exhaust Fan #17 Fault
b1 | Exhaust Fan #2 Fault | b1 | Exhaust Fan #18 Fault
b2 | Exhaust Fan #3 Fault | b2 | Exhaust Fan #19 Fault
b3 | Exhaust Fan #4 Fault | b3 | Exhaust Fan #20 Fault
b4 | Exhaust Fan #5 Fault | b4 | Exhaust Fan #21 Fault
b5 | Exhaust Fan #6 Fault | b5 | Exhaust Fan #22 Fault
b6 | Exhaust Fan #7 Fault | b6 | Exhaust Fan #23 Fault
b7 | Exhaust Fan #8 Fault | b7 | Exhaust Fan #24 Fault
b8 | Exhaust Fan #9 Fault | b8 | Exhaust Fan #25 Fault
b9 | Exhaust Fan #10 Fault | b9 | Exhaust Fan #26 Fault
b10 | Exhaust Fan #11 Fault | b10 | Exhaust Fan #27 Fault
b11 | Exhaust Fan #12 Fault | b11 | Exhaust Fan #28 Fault
b12 | Exhaust Fan #13 Fault | b12 | Exhaust Fan #29 Fault
b13 | Exhaust Fan #14 Fault | b13 | Exhaust Fan #30 Fault
b14 | Exhaust Fan #15 Fault | b14 | Exhaust Fan #31 Fault
b15 | Exhaust Fan #16 Fault | b15 | Exhaust Fan #32 Fault
AM internal status/flag #7 |  | AM internal status/flag #8
Bit | Description | Bit | Description
b0 | AM Fan #1 Fault | b0 | Main Ground Fault
b1 | AM Fan #2 Fault | b1 | Bypass Ground Fault
b2 |  | b2 | Output Ground Fault
b3 |  | b3 | Battery Ground Fault
b4 |  | b4
b5 |  | b5
b6 |  | b6
b7 |  | b7
b8 |  | b8
b9 |  | b9
b10 |  | b10
b11 |  | b11
b12 |  | b12
b13 |  | b13
b14 |  | b14
b15 |  | b15