## Worksheet
名称 | 编码 | 图标 | 设备可控 | 控制选项 | 属性 | 型号
温湿度传感器 | 1280 | icon-dial2 | 0 |  | {"as_time":"08:00~08:05","tn_field":"Tem","host_ip":"192.168.0.161","Tem":"℃","monitor":"istatus,温湿度状态,,;Tem,温度,0,℃;Hum,湿度,0,%","figure":",istatus,,;dial3,Tem,50,℃;dial3,Hum,100,%","exhibition":"istatus,温湿度状态,;Tem,温度,℃;Hum,湿度,%","briefing":"Tem,温度,℃;Hum,湿度,%","chart":"Tem,温度,℃;Hum,湿度,%","history":"Tem,温度,℃;Hum,湿度,%","statistics":"Tem","coefficient":"Tem,0.1;Hum,0.1"} | 1
区域漏水控制器（485方式） | 1536 | icon-water | 0 |  | {"monitor":"istatus,漏水状态,,;Status,漏水状态,4,","figure":",istatus,,;27,Status,1,","exhibition":"istatus,漏水状态,","briefing":"istatus,漏水状态,","chart":"istatus,漏水状态,","re_Status":"0,正常;1,告警"} | 2
空调控制器（单机版） | 1792 | icon-kongtiao3 | 1 | state;开关机;onoff;0;0,1;null ext3;温度;processbar;26;18,30;℃;tem mode;模式;radiogroup;制冷;制冷,制热;null btn;操作;button | {"monitor":"istatus,空调控制器,,;Hfkwd,回风温度,0,℃;Sfkwd,送风温度,0,℃;Ht,上限温度,,;Lt,下限温度,,;Ct,设置温度,,;Dl,当前电流,,A;Hdl,电流上限,,A;Ldl,电流下限,,A;StatusV,当前状态,4,","figure":",istatus,,;05,Hfkwd,50,℃;06,Sfkwd,50,℃;,Ht,,;,Lt,,;,Ct,,;,Dl,,A;,Hdl,,A;,Ldl,,A;03,StatusV,,","exhibition":"istatus,空调控制器,;Hfkwd,回风温度,℃;Sfkwd,送风温度,℃","briefing":"Hfkwd,回风温度,℃;Sfkwd,送风温度,℃;StatusV,当前状态,","chart":"istatus,空调控制器,","coefficient":"Hfkwd,0.01;Sfkwd,0.01;Dl,0.01;Hdl,0.01;Ldl,0.01","re_StatusV":"0,关机;1,制冷;2,制热"} | 1
艾默生精密空调PEX系列 | 2049 | icon-kongtiao4 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,精密空调状态,,;tem,室内温度,0,℃;hum,室内湿度,0,%;va,A相电压,,V;vb,B相电压,,V;vc,C相电压,,V;c,加湿器电流,,A;pl,电源频率,,;hftemset,回风温度设定点,,℃;temset,送风温度设定点,,℃;temoff,温度偏差,,℃;humoff,湿度偏差,,;temdead,温度死区,,;humdead,湿度死区,,;htemw,高温告警值,,;ltemw,低温告警值,,;hhumw,高湿告警值,,;lhumw,低湿告警值,,;sftemw,送风高温告警值,,;sftemset,送风温度设定点,,;status,空调状态,,;warn,报警状态,,;stfansw,风机输出开关状态,,;sthumisw,加湿器输出开关状态,,;stcomp1sw,压缩机1输出开关状态,,;stcomp2sw,压缩机2输出开关状态,,;stheater1sw,加热1输出开关状态,,;stheater2sw,加热2输出开关状态,,;stalmswsw,公共报警输出开关状态,,;stwbybass1sw,液路旁通1输出开关状态,,;stwbybass2sw,液路旁通2输出开关状态,,;stwatersw,注水输出开关状态,,;stdehumisw,除湿输出开关状态,,;streservesw,备用输出开关状态,,;stcomp1ressw,压缩机1反相输出开关状态,,;stcomp2ressw,压缩机2反相输出开关状态,,;stcool,制冷状态,,;stheat,加热状态,,;stdehumi,除湿状态,,;sthumi,加湿状态,,","figure":",istatus,,;dial3,tem,,℃;dial3,hum,,%;,va,,V;,vb,,V;,vc,,V;,c,,A;,pl,,;,hftemset,,℃;,temset,,℃;,temoff,,℃;,humoff,,;,temdead,,;,humdead,,;,htemw,,;,ltemw,,;,hhumw,,;,lhumw,,;,sftemw,,;,sftemset,,;,status,,;,warn,,;,stfansw,,;,sthumisw,,;,stcomp1sw,,;,stcomp2sw,,;,stheater1sw,,;,stheater2sw,,;,stalmswsw,,;,stwbybass1sw,,;,stwbybass2sw,,;,stwatersw,,;,stdehumisw,,;,streservesw,,;,stcomp1ressw,,;,stcomp2ressw,,;,stcool,,;,stheat,,;,stdehumi,,;,sthumi,,","exhibition":"istatus,精密空调状态,;tem,室内温度,℃;hum,室内湿度,%"} | 0
声光报警器 | 2304 | icon-23 | 1 |  | {"iDo":"1"} | 0
DO1控制 | 2304 | icon-23 | 0 |  | {"as_time":"08:00~08:05"} | 1
DO2控制 | 2304 | icon-23 | 0 |  | {"host_ip":"192.168.0.161","as_time":"08:00~08:05"} | 2
三相电量仪 | 256 | icon-18 | 0 |  | {"monitor":"istatus,市电状态,,;Ygzdn,总电能,,KWH;Zyggl,总有功功率,,W;Zwggl,总无功功率,,Var;Zszgl,总视载功率,,VA;Zglys,总功率因素,,;Ady,A相电压,0,V;Bdy,B相电压,0,V;Cdy,C相电压,0,V;Adl,A相电流,0,A;Bdl,B相电流,0,A;Cdl,C相电流,0,A","figure":",istatus,,;,Ygzdn,,KWH;,Zyggl,,W;,Zwggl,,Var;,Zszgl,,VA;,Zglys,,;meter,Ady,300,V;meter,Bdy,300,V;meter,Cdy,300,V;meter,Adl,100,A;meter,Bdl,100,A;meter,Cdl,100,A","exhibition":"istatus,市电状态,;Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","briefing":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V;Adl,A相电流,A;Bdl,B相电流,A;Cdl,C相电流,A","history":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","coefficient":"Ygzdn,0.001;Zglys,0.001;Ady,0.1;Bdy,0.1;Cdy,0.1;Adl,0.01;Bdl,0.01;Cdl,0.01","re_istatus":"1,正常;0,告警"} | 0
单相电量仪 | 256 | icon-18 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,市电状态,,;Ygzdn,总电能,,KWH;Ayggl,有功功率,,W;Awggl,无功功率,,Var;Aszgl,视在功率,,VA;Aglys,功率因数,,;Ady,电压,0,V;Adl,电流,0,A","figure":",istatus,,;,Ygzdn,,KWH;,Ayggl,,W;,Awggl,,Var;,Aszgl,,VA;,Aglys,,;meter,Ady,300,V;meter,Adl,50,A","exhibition":"istatus,市电状态,;Ady,电压,V;Adl,电流,A","briefing":"Ady,电压,V;Adl,电流,A","statistics":"Ygzdn;Ady;Adl","coefficient":"Ygzdn,0.001;Ayggl,0.1;Awggl,0.1;Aszgl,0.1;Ady,0.1;Adl,0.1"} | 35
NVR | 3078 | icon-19 | 0 |  | {"as_time":"08:00~08:05"} | 0
门禁 | 3331 | icon-16 | 0 |  | {"as_time":"08:00~08:05","monitor":"Door,,,","figure":",istatus,,;,Rec,,;,Card,,;29,Door,,;,St,,;,LogDate,,","exhibition":"Door,,","chart":"Door,,","statistics":"Door","eq_log":"istatus,;Rec,;Card,;Door,;St,;LogDate,"} | 0
ping ip | 3335 | icon-host2 | 0 |  | {"monitor":"iPingState,IP状态,4,","figure":",istatus,,;,iPingState,,","exhibition":"iPingState,IP状态,","re_iPingState":"1,在线;0,离线"} | 0
红外探测器 | 3590 | icon-hongwai2 | 0 |  | {"monitor":"istatus,红外状态,4,","figure":"14,istatus,1,","exhibition":"istatus,红外状态,","briefing":"istatus,红外状态,"} | 0
烟雾探测器 | 3591 | icon-20 | 0 |  | {"1122":"111","as_time":"08:00~08:05","monitor":"istatus,烟感状态,4,","figure":"13,istatus,1,","exhibition":"istatus,烟感状态,","briefing":"istatus,烟感状态,","re_istatus":"0,正常;1,告警"} | 0
区域漏水控制器（开关量） | 3592 | icon-water | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,漏水监测,4,","figure":"12,istatus,1,","exhibition":"istatus,漏水监测,","briefing":"istatus,漏水监测,"} | 0
门磁开关 | 3593 | icon-15 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,门磁状态,4,","figure":",istatus,,","exhibition":"istatus,门磁状态,","chart":"istatus,门磁状态,","eq_log":"istatus,门磁状态"} | 0
蓄电池监测（管理模块） | 4609 | icon-ec2 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,蓄电池状态,,;V40004,蓄电池1#,0,V;V40005,蓄电池2#,0,V;V40006,蓄电池3#,0,V;V40307,蓄电池内阻1#,0,MΩ;V40308,蓄电池2#,0,MΩ;V40309,蓄电池3#,0,MΩ;V40910,蓄电池温度1#,0,℃;V40911,蓄电池温度2#,0,℃;V40912,蓄电池温度3#,0,℃;V41817,电池组电压,0,V;V41818,充放电电流,0,A;V41821,环境温度,0,℃;V41823,最高电压电池,,#;V41824,最低电压电池,,#;V41825,最高内阻电池,,#;V41826,电压均差值,,MV;V41827,电压均差值,,MV;V41833,整组状态,4,","figure":",istatus,,;,V40004,,V;,V40005,,V;,V40006,,V;,V40007,,V;,V40307,,MΩ;,V40308,,MΩ;,V40309,,MΩ;,V40310,,MΩ;,V40910,,℃;,V40911,,℃;,V40912,,℃;,V40913,,℃;meter,V41817,100,V;meter,V41818,50,A;,V41821,,℃;,V41823,,#;,V41824,,#;,V41825,,#;,V41826,,MV;,V41827,,MV;,V41833,,","exhibition":"istatus,蓄电池状态,;V41817,电池组电压,V;V41818,充放电电流,A","chart":"V40004,蓄电池1#,V;V40005,蓄电池2#,V;V40006,蓄电池3#,V;V40307,蓄电池内阻1#,MΩ;V40308,蓄电池2#,MΩ;V40309,蓄电池3#,MΩ;V40310,蓄电池4#,MΩ;V40910,蓄电池温度1#,℃;V40911,蓄电池温度2#,℃;V40912,蓄电池温度3#,℃","coefficient":"V40004,0.001;V40005,0.001;V40006,0.002;V40007,0.001;V40307,0.001;V40308,0.001;V40309,0.001;V40310,0.001;V40910,0.1;V40911,0.1;V40912,0.1;V40913,0.1;V41817,0.1;V41818,0.1","bar_0":"V400;电压;04;32;#e6e10e","bar_1":"V403;电阻;07;32;#34d417","bar_2":"V409;温度;10;32;#21d9f3","re_V41833":"0, 正常;1,告警"} | 0
配电空开监测仪 | 512 | icon-ec4 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,配电检测状态,,;sd1,空开1,4,;sd2,空开2,4,;sd3,空开3,4,;sd4,空开4,4,;sd5,空开5,4,;sd6,空开6,4,","figure":",istatus,,;01,sd1,0,;01,sd2,0,;01,sd3,0,;01,sd4,0,;01,sd5,0,;01,sd6,0,","exhibition":"istatus,配电检测状态,","briefing":"sd1,空开1,;sd2,空开2,;sd3,空开3,;sd4,空开4,;sd5,空开5,;sd6,空开6,","re_sd1":"0,闭合;1,断开","re_sd2":"0,闭合;1,断开","re_sd3":"0,闭合;1,断开","re_sd4":"0,闭合;1,断开","re_sd5":"0,闭合;1,断开","re_sd6":"0,闭合;1,断开"} | 0
山特3KVA UPS | 768 | icon-22 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,UPS状态,,;Vin1,输入电压,0,V;Fin,输入频率,,Hz;Vout,输出电压,0,V;Aout,输出负载,,%;Tem,环境温度,,℃;b7,蜂鸣器,,;b6,UPS状态,,;b5,UPS模式,,;b4,机型属性,,;b3,UPS故障,,;b2,旁路模式,,;b1,电池电压,,;b0,市电电压,,;Vbatt,电池电压,,V","figure":",istatus,,;meter,Vin1,300,V;,Fin,,Hz;meter,Vout,250,V;26,Aout,,%;,Tem,,℃;,b7,,;,b6,,;,b5,,;,b4,,;,b3,,;,b2,,;,b1,,;,b0,,;,Vbatt,,V","exhibition":"istatus,UPS状态,;Vin1,输入电压,V;Vout,输出电压,V","briefing":"Vin1,输入电压,V;Vout,输出电压,V;Aout,输出负载,%","coefficient":"Vin1,0.1;Fin,0.1;Vout,0.1;Aout,0.1;Tem,0.1;Vbatt,0.01","re_b7":"0,关闭;1,开启","re_b6":"0,关闭;1,开启","re_b5":"0,非测试;1,测试","re_b4":"0,在线式;1,后备式","re_b3":"0,否;1,是","re_b2":"0,否;1,是","re_b1":"0,正常;1,低电压","re_b0":"0,正常;1,异常"} | 0
门禁 | 300000 | icon-16 | 0 |  | {"wg_login":"http://192.168.1.157:8400/ACT_ID_1","wg_username":"Szubnt","wg_password":"SZYWztf@123"} | 0
动环监控主机 | 0 | icon-17 | 0 |  | {"host_ip":"192.168.10.161","monitor":"cpu1,平均负载,,%;cpu5,近5分钟平均负载,,%;cpu15,近15分钟平均负载,,%;memtotal,总内存,,KB;memfree,剩余内存,,KB;membuf,缓冲内存,,KB;memcach,缓存内存,,KB","figure":",istatus,,;26,cpu1,100,%;26,cpu5,,%;26,cpu15,,%;,memtotal,512000,KB;,memfree,,KB;,membuf,,KB;,memcach,,KB","exhibition":"istatus,监控主机,","coefficient":"cpu1,0.1;cpu5,0.1;cpu15,0.1;memtotal,1;memfree,1;membuf,1;memcach,1"} | 0
海康视频 | 200000 | icon-19 | 0 |  | {"hk_ip":"182.0.0.","hk_port":"80","hk_username":"admin","hk_password":"admln12345","hk_channels":"1","hk_eqport":"8000"} | 0
萤石视频 | 100000 | icon-19 | 0 |  | {"hls":"1","deviceSerial":"1","channelNo":"1"} | 0
铁锂电池 | 1041 | icon-ec2 | 0 |  | {"monitor":"istatus,,,;Volt1,电池电压,0,V;AllCap1,容量,0,;SOH1,SOH,,","figure":",istatus,,;meter,Volt1,300,V;,AllCap1,,;,SOH1,,","briefing":"Volt1,电池电压,V","history":"Volt1,电池电压,V","statistics":"Volt1","coefficient":"Volt1,0.1","bar_0":"Volt;电压;1;1;#FFBB66","bar_1":"SOH;SOH;1;1;#FF5511 ","bar_2":"AllCap;容量;1;1;#00DDDD"} | 0
空调控制器 | 4944 | icon-kongtiao3 | 0 |  | {"monitor":"istatus,状态,,;V40001,当前湿度,0,%;V40002,当前温度,0,°C","figure":"03,istatus,,;28,V40001,,%;28,V40002,,°C","exhibition":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,°C","briefing":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,°C","history":"V40001,当前湿度,%;V40002,当前温度,°C","coefficient":"V40001,0.1;V40002,0.1"} | 1
网络监测 | 400000 | icon-17 | 0 |  | {"ping_ip":"192.168.0.161"} | 0
蓄电池监测（1180） | 1044 | icon-ec2 | 0 |  | {"monitor":"istatus,状态,,;Vol,电压,,V;Reg,内阻,,mΩ;Tem,温度,, ℃","figure":",istatus,,;,Vol0,,V;,Reg0,,mΩ;,Tem0,,℃;meter,Vol,,V;meter,Reg,,mΩ;,Tem,, ℃","coefficient":"Vol0,0.001;Reg0,0.0001;Tem0,0.01;Vol,0.001;Reg,0.0001;Tem,0.1","exhibition":"istatus,状态,","chart":"istatus,状态,","history":"istatus,状态,"} | 0
精密空调-艾默生 | 2056 | icon-kongtiao4 | 0 |  | {"monitor":"istatus,状态,,;s_fj,风机,4,;s_zl,制冷状态,4,;s_jrq,加热器,4,;s_jsq,加湿器 ,4,;s_csj,除湿器,4,;r_tem,回风温度,0,;r_hum,回风湿度,0,%RH;temset,设定温度,0,℃;humset,设定湿度,0,%RH","figure":",istatus,,;,s_fj,,;,s_zl,,;,s_jrq,,;,s_jsq,,;,s_csj,,;dial3,r_tem,,;dial3,r_hum,,%RH;dial3,temset,,℃;dial3,humset,,%RH","exhibition":"istatus,状态,;r_tem,回风温度,;r_hum,回风湿度,%RH;temset,设定温度,℃;humset,设定湿度,%RH","briefing":"istatus,状态,;r_tem,回风温度,;r_hum,回风湿度,%RH;temset,设定温度,℃;humset,设定湿度,%RH","history":"r_tem,回风温度,;r_hum,回风湿度,%RH;temset,设定温度,℃;humset,设定湿度,%RH","coefficient":"r_tem,0.1;r_hum,1;temset,0.1;humset,1","re_s_fj":"0,关闭;1,开启","re_s_zl":"0,关闭;1,开启","re_s_jrq":"0,关闭;1,开启","re_s_jsq":"0,关闭;1,开启","re_s_csj":"0,关闭;1,开启"} | 0
空调控制器-新版 | 4944 | icon-kongtiao4 | 1 | cmdid;电源;radiogroup;制冷开机;制冷开机,制热开机,关机;null cold;制冷温度;processbar;18;18,27;℃;null hot;制热温度;processbar;18;18,27;℃;null | {"monitor":"istatus,状态,,;V40001,当前湿度,,%;V40002,当前温度,,°C","figure":",istatus,,;dial3,V40001,,%;dial3,V40002,,°C","exhibition":"V40001,当前湿度,%;V40002,当前温度,°C","briefing":"V40001,当前湿度,%;V40002,当前温度,°C","chart":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,°C","coefficient":"V40001,0.1;V40002,0.1"} | 0
温湿度传感器（旧款） | 1280 | icon-dial2 | 0 |  | {"tn_field":"Tem","as_time":"08:00~08:05","monitor":"istatus,温湿度状态,,;Tem,温度,4,℃;Hum,湿度,0,%","figure":",istatus,,;dial3,Tem,,℃;dial3,Hum,,%","exhibition":"istatus,温湿度状态,;Tem,温度,℃;Hum,湿度,%","briefing":"Tem,温度,℃;Hum,湿度,%","chart":"Tem,温度,℃;Hum,湿度,%","history":"Tem,温度,℃;Hum,湿度,%","coefficient":"Tem,0.1;Hum,0.1"} | 0
施耐德UPS-modbus | 4691 | icon-22 | 0 |  | {"monitor":"V410001,旁路相电压A,0,V;V410002,旁路相电压B,0,V;V410003,旁路相电压C,0,V;V410004,旁路相电流A,0,A;V410005,旁路相电流B,0,A;V410006,旁路相电流C,0,A;V410007,旁路频率A,0,HZ;V410008,旁路频率B,0,HZ;V410009,旁路频率C,0,HZ;V410013,输入相电压A,0,V;V410014,输入相电压B,0,V;V410015,输入相电压C,0,V;V410016,输入相电流A,0,A;V410017,输入相电流B,0,A;V410018,输入相电流C,0,A;V410019,输入频率A,0,HZ;V410020,输入频率B,0,HZ;V410021,输入频率,0,HZ;V410025,输出相电压A,0,V;V410026,输出相电压B,0,V;V410027,输出相电压C,0,V;V410028,输出相电流A,0,A;V410029,输出相电流B,0,A;V410030,输出相电流C,0,A;V410031,输出频率A,0,HZ;V410032,输出频率B,0,HZ;V410033,输出频率,0,HZ;V410037,有功功率A,0,kW;V410038,有功功率B,0,kW;V410039,有功功率C,0,kW;V410040,无功功率A,0,kVar;V410041,无功功率B,0,kVar;V410042,无功功率C,0,kVar;V410043,视在功率A,0,kVA;V410044,视在功率B,0,kVA;V410045,视在功率C,0,kVA;V410050,正电池组电压,0,V;V410051,负电池组电压,0,V;V410052,正电池组电流,0,A;V410053,负电池组电流,0,A;V410054,电池温度,0,℃;V410055,电池剩余时间,0,min;V410056,电池容量,0,%;V410110,电池状态,,;V410111,电池连接状态,,;V410119,旁路过载,4,;V410128,电池电压低,4,;V410130,整流器状态,,;V410131,逆变器状态,,;V410134,整流器故障,,;V410135,逆变器故障,,;V410136,整流器过温,4,;V410137,风扇故障,4,;V410138,逆变器过载,4,;V410139,逆变器过温,4,","figure":",V410001,,V;,V410002,,V;,V410003,,V;,V410004,,A;,V410005,,A;,V410006,,A;,V410007,,HZ;,V410008,,HZ;,V410009,,HZ;meter,V410013,250,V;meter,V410014,250,V;meter,V410015,250,V;,V410016,,A;,V410017,,A;,V410018,,A;,V410019,,HZ;,V410020,,HZ;,V410021,,HZ;meter,V410025,250,V;meter,V410026,250,V;meter,V410027,250,V;,V410028,,A;,V410029,,A;,V410030,,A;,V410031,,HZ;,V410032,,HZ;,V410033,,HZ;,V410037,,kW;,V410038,,kW;,V410039,,kW;,V410040,,kVar;,V410041,,kVar;,V410042,,kVar;,V410043,,kVA;,V410044,,kVA;,V410045,,kVA;,V410050,,V;,V410051,,V;,V410052,,A;,V410053,,A;,V410054,,℃;,V410055,,min;,V410056,,%;,V410110,,;,V410111,,;,V410119,,;,V410128,,;,V410130,,;,V410131,,;,V410134,,;,V410135,,;,V410136,,;,V410137,,;,V410138,,;,V410139,,","exhibition":"V410013,输入相电压A,V;V410014,输入相电压B,V;V410015,输入相电压C,V;V410025,输出相电压A,V;V410026,输出相电压B,V;V410027,输出相电压C,V","briefing":"V410013,输入相电压A,V;V410014,输入相电压B,V;V410015,输入相电压C,V;V410025,输出相电压A,V;V410026,输出相电压B,V","history":"V410013,输入相电压A,V;V410014,输入相电压B,V;V410015,输入相电压C,V;V410025,输出相电压A,V;V410026,输出相电压B,V;V410027,输出相电压C,V","coefficient":"V410001,0.1;V410002,0.1;V410003,0.1;V410004,0.1;V410005,0.1;V410006,0.1;V410007,0.01;V410008,0.01;V410009,0.01;V410013,0.1;V410014,0.1;V410015,0.1;V410016,0.1;V410017,0.1;V410018,0.1;V410019,0.01;V410020,0.01;V410021,0.01;V410025,0.1;V410026,0.1;V410027,0.1;V410028,0.1;V410029,0.1;V410030,0.1;V410031,0.01;V410032,0.01;V410033,0.01;V410037,0.1;V410038,0.1;V410039,0.1;V410040,0.1;V410041,0.1;V410042,0.1;V410043,0.1;V410044,0.1;V410045,0.1;V410050,0.1;V410051,0.1;V410052,0.1;V410053,0.1;V410054,0.1;V410055,0.1;V410056,0.1","re_V410110":"0,未工作;1,浮充;2,均充;3,放电","re_V410111":"0,已连接;1,断开","re_V410119":"0,正常;1,过载","re_V410128":"0,正常;1,过低","re_V410130":"0,关;1,软启动;2,正常工作","re_V410131":"0,关;1,软启动;2,正常工作","re_V410134":"0,正常;1,故障","re_V410135":"0,正常;1,故障","re_V410136":"0,正常;1,报警","re_V410137":"0,正常;1,故障","re_V410138":"0,正常;1,故障","re_V410139":"0,正常;1,过温"} | 0
施耐德UPS-SNMP | 808 | icon-22 | 0 |  | {"monitor":"istatus,状态,,;Vin1,输入电压A,0,V;Vin2,输入电压B,0,V;Vin3,输入电压C,0,V;Vout1,输出电压A,0,V;Vout2,输出电压B,0,V;Vout3,输入电压C,0,V;VB1,输出功率A,,W;VB2,输出功率B,,W;VB3,输出功率C,,W;Fin1,输入频率,,HZ;Fout1,输出频率,,HZ;Pout1,输出负载A,,%;Pout2,输出负载B,,%;Pout3,输出负载C,,%;Tem,电池温度,,℃;b15,UPS 异常,4,;b7,UPS过载,4,;b2,旁路内部故障,4,;b1,旁路供电故障,4,;b0,旁路风扇故障,4,;Vbatt,电池电压,,V;Pbatt,电池容量,,%","figure":",istatus,,;meter,Vin1,250,V;meter,Vin2,250,V;meter,Vin3,250,V;meter,Vout1,250,V;meter,Vout2,250,V;meter,Vout3,250,V;,VB1,,W;,VB2,,W;,VB3,,W;,Fin1,,HZ;,Fout1,,HZ;,Pout1,,%;,Pout2,,%;,Pout3,,%;,Tem,,℃;,b15,,;,b7,,;,b2,,;,b1,,;,b0,,;,Vbatt,,V;,Pbatt,,%","exhibition":"Vin1,输入电压A,V;Vin2,输入电压B,V;Vin3,输入电压C,V;Vout1,输出电压A,V;Vout2,输出电压B,V;Vout3,输入电压C,V","briefing":"Vin1,输入电压A,V;Vin2,输入电压B,V;Vin3,输入电压C,V;Vout1,输出电压A,V;Vout2,输出电压B,V;Vout3,输入电压C,V","history":"Vin1,输入电压A,V;Vin2,输入电压B,V;Vin3,输入电压C,V;Vout1,输出电压A,V;Vout2,输出电压B,V;Vout3,输入电压C,V","coefficient":"Vin1,0.1;Vin2,0.1;Vin3,0.1;Vout1,0.1;Vout2,0.1;Vout3,0.1;VB1,0.1;VB2,0.1;VB3,0.1;Fin1,0.1;Fout1,0.1;Pout1,0.1;Pout2,0.1;Pout3,0.1;Tem,0.1;Vbatt,0.1;Pbatt,0.1","re_istatus":"0,正常;1,告警","re_b15":"0,正常;1,告警","re_b7":"0,正常;1,过载","re_b2":"0,正常;1,告警","re_b1":"0,正常;1,告警","re_b0":"0,正常;1,告警"} | 0
电池检测 | 1044 | icon-ec2 | 0 |  | {"bar_0":"Vot;电压;1;32;#e6e10e","bar_1":"Reg;内阻;1;32;#34d417","bar_2":"Tem;温度;1;32;#21d9f3"} | 16
UPS监测-华为 | 790 | icon-22 | 0 |  | {"monitor":"istatus,UPS状态,,;Vin1,输入电压1,0,V;Vin2,输入电压2,0,V;Vin3,输入电压3,0,V;Vout1,输出电压1,0,V;Vout2,输出电压2,0,V;Vout3,输出电压3,0,V;Iin1,输入电流,0,A;Iin2,输入电流2,0,A;Iin3,输入电流3,0,A;Iout1,输出电流1,0,A;Iout2,输出电流2,0,A;Iout3,输出电流3,0,A;Fin1,输入频率,,HZ;Fout1,输出频率,,HZ;Tem,电池温度,,℃;b15,电池连接状态,4,;b14,整流器休眠状态,4,;b13,逆变器休眠状态,4,;b12,开机允许状态,4,;b11,逆变器告警状态,4,;b10,逆变器自检状态,4,;b9,逆变继电器状态,4,;b8,旁路告警状态,4,;b7,电池告警状态,4,;b6,电池自检状态,4,;b5,整流器限功率状态,4,;b4,放电器告警状态,4,;b3,旁路通讯失败,4,;b2,旁路配置失败,4,;b1,旁路供电状态,4,;b0,旁路接管状态,4,;Vbatt,电池电压,0,V;Pbatt,电池容量,0,%;Mbatt,电池剩余时间,,min","figure":",istatus,,;meter,Vin1,250,V;meter,Vin2,250,V;meter,Vin3,250,V;meter,Vout1,250,V;meter,Vout2,250,V;meter,Vout3,250,V;,Iin1,,A;,Iin2,,A;,Iin3,,A;,Iout1,,A;,Iout2,,A;,Iout3,,A;,Fin1,,HZ;,Fout1,,HZ;,Tem,,℃;,b15,,;,b14,,;,b13,,;,b12,,;,b11,,;,b10,,;,b9,,;,b8,,;,b7,,;,b6,,;,b5,,;,b4,,;,b3,,;,b2,,;,b1,,;,b0,,;,Vbatt,,V;,Pbatt,,%;,Mbatt,,min","exhibition":"Vin1,输入电压1,V;Vin2,输入电压2,V;Vin3,输入电压3,V;Vout1,输出电压1,V;Vout2,输出电压2,V;Vout3,输出电压3,V","briefing":"Vin1,输入电压1,V;Vin2,输入电压2,V;Vin3,输入电压3,V;Vout1,输出电压1,V;Vout2,输出电压2,V;Vout3,输出电压3,V","chart":"Vin1,输入电压1,V;Vin2,输入电压2,V;Vin3,输入电压3,V;Vout1,输出电压1,V;Vout2,输出电压2,V;Vout3,输出电压3,V","history":"Vin1,输入电压1,V;Vin2,输入电压2,V;Vin3,输入电压3,V;Vout1,输出电压1,V;Vout2,输出电压2,V;Vout3,输出电压3,V","coefficient":"Vin1,0.1;Vin2,0.1;Vin3,0.1;Vout1,0.1;Vout2,0.1;Vout3,0.1;Iin1,0.1;Iin2,0.1;Iin3,0.1;Iout1,0.1;Iout2,0.1;Iout3,0.1;Fin1,0.1;Fout1,0.1;Tem,0.1;Vbatt,0.1;Pbatt,0.1;Mbatt,0.1","re_b15":"0,未连接;1,已连接","re_b14":"0,非休眠;1,休眠","re_b13":"0,非休眠;1,休眠","re_b12":"0,不允许;1,允许","re_b11":"0,正常;1,告警","re_b10":"0,未自检;1,自检中","re_b9":"0,断开;1,闭合","re_b8":"0,正常;1,告警","re_b7":"0,否;1,是","re_b6":"0,否;1,是","re_b5":"0,未限功率;1,限功率","re_b4":"0,正常;1,告警","re_b3":"0,正常;1,通讯失败","re_b2":"0,正常;1,配置失败","re_b1":"0,非旁路供电;1,旁路供电","re_b0":"0,旁路没有接管;1,旁路被接管"} | 0
未命名的设备类型 | 3079 |  | 0 |  |  | 0
蓄电池检测（1044-1） | 1044 | icon-ec2 | 0 |  | {"monitor":"istatus,电池状态,,;Reg,内阻,,mΩ;Tem,温度,,℃;Vol,电压,,V","figure":",istatus,,;,Reg,,mΩ;,Tem,,℃;,Vol,,V","exhibition":"istatus,电池状态,","coefficient":"Reg,0.001;Tem,0.01;Vol,0.001"} | 1
双机空调控制器 | 1792 | icon-kongtiao3 | 1 | state;开关机;onoff;0;0,1;null ext3;温度;processbar;26;18,30;℃;tem mode;模式;radiogroup;制冷;制冷,制热;null btn;操作;button | {"monitor":"Ct,设置温度1,,;Ct2,设置温度2,,;Dl,当前电流1,,;Dl2,当前电流2,,;Hdl,电流上限1,,;Hdl2,电流上限2,,;Hfkwd,回风温度1,0,℃;Hfkwd2,回风温度2,0,℃;Ht,上限温度1,,;Ht2,上限温度2,,;istatus,空调控制器,,;Ldl,电流下限1,,A;Ldl2,电流下限2,,A;Lt,下限温度1,,℃;Lt2,下限温度2,,℃;Sfkwd,送风温度1,0,℃;Sfkwd2,送风温度2,0,℃;StatusV,当前状态1,4,;StatusV2,当前状态2,4,","figure":",Ct,,;,Ct2,,;,Dl,,;,Dl2,,;,Hdl,,;,Hdl2,,;dial3,Hfkwd,,℃;dial3,Hfkwd2,,℃;,Ht,,;,Ht2,,;,istatus,,;,Ldl,,A;,Ldl2,,A;,Lt,,℃;,Lt2,,℃;dial3,Sfkwd,,℃;dial3,Sfkwd2,,℃;,StatusV,,;,StatusV2,,","exhibition":"Hfkwd,回风温度1,℃;Hfkwd2,回风温度2,℃","briefing":"Hfkwd,回风温度1,℃;Hfkwd2,回风温度2,℃","coefficient":"Hfkwd,0.01;Hfkwd2,0.01;Ldl,0.01;Ldl2,0.01;Sfkwd,0.01;Sfkwd2,0.01","re_StatusV":"0,关机;1,制冷;2,制热","re_StatusV2":"0,关机;1,制冷;2,制热"} | 0
UPS | 4690 | icon-18 | 0 |  | {"monitor":"V411001,输入电压,,V;V411004,输入频率,,Hz;V411005,旁路电压频率,,V;V411008,旁路频率,,Hz;V411009,输出电压,,V;V411012,输出电流,,A;V411015,输出有功功率,,kw;V411016,输出视在功率,,kva;V411029,开机状态,,;V412001,电池电压,,V;V412003,电池状态,,;V412004,电池剩余容量,,%;V412005,电池后备时间,,s;V440157-3,内部过温,,;V440162-1,旁路电压异常,,;V440164-3,电池过压,,;V440165-1,电池需要维护,,;V440165-3,电池低压,,;V440174-5,输出过载,,;V440181-1,整流器异常,,;V440181-5,逆变器异常,,;V440183-4,充电器告警,,","figure":",V411001,,V;,V411004,,Hz;,V411005,,V;,V411008,,Hz;,V411009,,V;,V411012,,A;,V411015,,kw;,V411016,,kva;,V411029,,;,V412001,,V;,V412003,,;,V412004,,%;,V412005,,s;,V440157-3,,;,V440162-1,,;,V440164-3,,;,V440165-1,,;,V440165-3,,;,V440174-5,,;,V440181-1,,;,V440181-5,,;,V440183-4,,","exhibition":"V411001,输入电压,V","coefficient":"V411001,0.1;V411004,0.1;V411005,0.1;V411008,0.1;V411009,0.1;V411012,0.1;V411015,0.1;V411016,0.1","re_V411029":"0,关机;1,开机中;10,开机失败;11,开机完成;3,无","re_V412003":"2,休眠;3,浮充;4,均充;5,放电","re_V440157-3":"0,正常;1,告警","re_V440162-1":"0,正常;1,告警","re_V440164-3":"0,正常;1,告警","re_V440165-1":"0,正常;1,告警","re_V440165-3":"0,正常;1,告警","re_V440174-5":"0,正常;1,告警","re_V440181-1":"0,正常;1,告警","re_V440181-5":"0,正常;1,告警","re_V440183-4":"0,正常;1,告警"} | 0
市电检测 | 4841 | icon-18 | 0 |  | [] | 0
APC-UPS | 771 | icon-22 | 0 |  | {"monitor":"Fout,输出频率,,Hz;Mbatt,电池剩余时间,,min;Pbatt,电池容量,,%;Pout,负载功率,,%;v1,最大输入电压,,V;v2,最小输入电压,,V;Vbatt,电池当前电压,,V;Vdc,蓄电池额定电压,,V;Vin1,当前输入电压,,V","figure":",Fout,,Hz;,Mbatt,,min;,Pbatt,,%;,Pout,,%;,v1,,V;,v2,,V;,Vbatt,,V;,Vdc,,V;,Vin1,,V","exhibition":"Vin1,当前输入电压,V","coefficient":"Fout,0.1;Pbatt,0.1;v1,0.1;v2,0.1;Vbatt,0.1;Vin1,0.1"} | 0
空调控制器 | 1792 | icon-kongtiao3 | 0 |  | [] | 2
蓄电池监测 | 1029 | icon-ec2 | 0 |  | {"monitor":"Vol7,电池电压7,,V;Vol8,电池电压8,,V;Volt,电池电压,,V;State7,电池状态7,,;State8,电池状态8,,;Tem1,电池温度1,,℃;Tem2,电池温度2,,℃;Tem3,电池温度3,,℃;Tem4,电池温度4,,℃;Tem5,电池温度5,,℃;Tem6,电池温度6,,℃;Tem7,电池温度7,,℃;Tem8,电池温度8,,℃;Vol1,电池电压1,,V;Vol2,电池电压2,,V;Vol3,电池电压3,,V;Vol4,电池电压4,,V;Vol5,电池电压5,,V;Vol6,电池电压6,,V;Reg1,电池内阻1,,mΩ;Reg2,电池内阻2,,mΩ;Reg3,电池内阻3,,mΩ;Reg4,电池内阻4,,mΩ;Reg5,电池内阻5,,mΩ;Reg6,电池内阻6,,mΩ;Reg7,电池内阻7,,mΩ;Reg8,电池内阻8,,mΩ;State1,电池状态1,,;State2,电池状态2,,;State3,电池状态3,,;State4,电池状态4,,;State5,电池状态5,,;State6,电池状态6,,","figure":",Vol7,,V;,Vol8,,V;,Volt,,V;,State7,,;,State8,,;,Tem1,,℃;,Tem11,,℃;,Tem12,,℃;,Tem13,,℃;,Tem14,,℃;,Tem15,,℃;,Tem16,,℃;,Tem17,,℃;,Tem18,,℃;,Tem19,,℃;,Tem2,,℃;,Tem25,,℃;,Tem26,,℃;,Tem27,,℃;,Tem28,,℃;,Tem29,,℃;,Tem3,,℃;,Tem30,,℃;,Tem31,,℃;,Tem32,,℃;,Tem4,,℃;,Tem5,,℃;,Tem6,,℃;,Tem7,,℃;,Tem8,,℃;,Vol1,,V;,Vol11,,V;,Vol12,,V;,Vol13,,V;,Vol14,,V;,Vol15,,V;,Vol16,,V;,Vol17,,V;,Vol18,,V;,Vol19,,V;,Vol2,,V;,Vol25,,V;,Vol26,,V;,Vol27,,V;,Vol28,,V;,Vol29,,V;,Vol3,,V;,Vol30,,V;,Vol31,,V;,Vol32,,V;,Vol4,,V;,Vol5,,V;,Vol6,,V;,Reg1,,mΩ;,Reg11,,mΩ;,Reg12,,mΩ;,Reg13,,mΩ;,Reg14,,mΩ;,Reg15,,mΩ;,Reg16,,mΩ;,Reg17,,mΩ;,Reg18,,mΩ;,Reg19,,mΩ;,Reg2,,mΩ;,Reg25,,mΩ;,Reg26,,mΩ;,Reg27,,mΩ;,Reg28,,mΩ;,Reg29,,mΩ;,Reg3,,mΩ;,Reg30,,mΩ;,Reg31,,mΩ;,Reg32,,mΩ;,Reg4,,mΩ;,Reg5,,mΩ;,Reg6,,mΩ;,Reg7,,mΩ;,Reg8,,mΩ;,State1,,;,State2,,;,State3,,;,State30,,;,State4,,;,State5,,;,State6,,","coefficient":"Vol7,0.001;Vol8,0.001;Volt,0.001;Tem1,0.1;Tem11,0.1;Tem12,0.1;Tem13,0.1;Tem14,0.1;Tem15,0.1;Tem16,0.1;Tem17,0.1;Tem18,0.1;Tem19,0.1;Tem2,0.1;Tem25,0.1;Tem26,0.1;Tem27,0.1;Tem28,0.1;Tem29,0.1;Tem3,0.1;Tem30,0.1;Tem31,0.1;Tem32,0.1;Tem4,0.1;Tem5,0.1;Tem6,0.1;Tem7,0.1;Tem8,0.1;Vol1,0.001;Vol11,0.001;Vol12,0.001;Vol13,0.001;Vol14,0.001;Vol15,0.001;Vol16,0.001;Vol17,0.001;Vol18,0.001;Vol19,0.001;Vol2,0.001;Vol25,0.001;Vol26,0.001;Vol27,0.001;Vol28,0.001;Vol29,0.001;Vol3,0.001;Vol30,0.001;Vol31,0.001;Vol32,0.001;Vol4,0.001;Vol5,0.001;Vol6,0.001;Reg1,0.001;Reg11,0.001;Reg12,0.001;Reg13,0.001;Reg14,0.001;Reg15,0.001;Reg16,0.001;Reg17,0.001;Reg18,0.001;Reg19,0.001;Reg2,0.001;Reg25,0.001;Reg26,0.001;Reg27,0.001;Reg28,0.001;Reg29,0.001;Reg3,0.001;Reg30,0.001;Reg31,0.001;Reg32,0.001;Reg4,0.001;Reg5,0.001;Reg6,0.001;Reg7,0.001;Reg8,0.001","bar_0":"Vol;电压;1;32;#e6e10e","bar_1":"Reg;内阻;1;32;#34d417","bar_2":"Tem;温度;1;32;#21d9f3","re_State11":"0,正常;2,离线","re_State12":"0,正常;2,离线","re_State13":"0,正常;2,离线","re_State14":"0,正常;2,离线","re_State15":"0,正常;2,离线","re_State16":"0,正常;2,离线","re_State17":"0,正常;2,离线","re_State18":"0,正常;2,离线","re_State19":"0,正常;2,离线","re_State25":"0,正常;2,离线","re_State26":"0,正常;2,离线","re_State27":"0,正常;2,离线","re_State28":"0,正常;2,离线","re_State29":"0,正常;2,离线","re_State31":"0,正常;2,离线","re_State32":"0,正常;2,离线","re_State7":"0,正常;2,离线","re_State8":"0,正常;2,离线","re_State1":"0,正常;2,离线","re_State2":"0,正常;2,离线","re_State3":"0,正常;2,离线","re_State30":"0,正常;2,离线","re_State4":"0,正常;2,离线","re_State5":"0,正常;2,离线","re_State6":"0,正常;2,离线"} | 0
未命名的设备类型 | 2304 |  | 0 |  |  | 3